## BOQ
Item Rate BoQ
Tender Inviting Authority: Airports Authority of India
Name of Work: Reconstruction of Old Terminal Building at Pune Airport. Sub Head: Revamping of part old Terminal Building and Miscellaneous works for enhancing total passenger handling capacity at Pune Airport.
Contract No: 2024_AAI_203069
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | BASIC RATE | TOTAL AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | SH I - Civil
2 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth for leads beyond Municipal limits and lift upto 1.5 m, as directed by Engineer-in-charge.All kinds of soil | 625 | cum |  | 0
3 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth for leads beyond Municipal limits and lift upto 1.5 m, as directed by Engineer-in-charge.Hard rock (blasting prohibited) | 313 | cum |  | 0
4 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m :Pipes, cables etc. exceeding 80 mm dia. but not exceeding 300 mm dia | 100 | metre |  | 0
5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:2:4 (1 cement : 2 Manufactured sand : 4 graded stone aggregate 20 mm nominal size) | 10 | cum |  | 0
6 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :a) 1:4:8 (1 Cement : 4 manufactured sand : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | 42 | cum |  | 0
7 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 Manufactured sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 19 | cum |  | 0
8 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level.a) Thermo-Mechanically Treated bars of grade Fe-500D or more. | 21100 | kg |  | 0
9 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering,finishing and reinforcement as per direction of the engineer-in-charge; for thefollowing grades of concrete.Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately.In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.All works upto plinth levelConcrete of M25 grade with minimum cement content of 330 kg /cum | 160 | cum |  | 0
10 | Brick work with F.P.S. (non modular) Fly Ash bricks of class designation 7.5 in foundation and plinth in:Cement mortar 1:6 (1 Cement : 6 coarse sand) | 10 | cum |  | 0
11 | Extra for providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brick masonry. | 100 | sqm |  | 0
12 | Brick work with flyash F.P.S. (non modular) brick of class designation 7.5 in superstructure above plinth level up to floor five level in :a) Cement mortar 1:6 (1 cement : 6 Coarse sand) | 293 | cum |  | 0
13 | Half brick masonry with non modular fly ash bricks of class designation 7.5, conformingio IS :12894, in super structure above plinth and upto floor V level.a) Cement mortar 1 : 4 (1 cement : 4 Manufactured sand) | 100 | sqm |  | 0
14 | Stone tile work for wall lining upto 10 m height with special adhesive over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand), including pointing in white cement with an admixture of pigment to match the stone shade.a) 20 mm thick (mirror polished and machine cut edge) Granite stone of any colour and shade | 99 | sqm |  | 0
15 | Providing edge moulding to 18 mm thick marble/ granite stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-charge.a) Granite work | 600 | mtr |  | 0
16 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 432 | sqm |  | 0
17 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 plyveneering with vertical grains or cross bands and face veneers on both faces of shutters:35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws | 6 | sqm |  | 0
18 | Providing and fixing 18mm thick both sides Pre-laminated cement bonded wood particle board as per IS : 15786:2008 of approved brand and shade with suitable full threaded steel screws etc. in partitions, boxes, shelves, racks and cupboard, kitchen cabinet under kitchen counter etc. all complete as per direction of Engineer-in-charge (Note: Fittings to be paid separately).a)18 mm thick | 100 | sqm |  | 0
19 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 100 | kg |  | 0
20 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.Electric resistance or induction butt welded tubes | 6500 | kg |  | 0
21 | Providing and laying Vitrified tiles in floor in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only . Laying of tiles will be done with the notch trowel, plier, wedge, clips of required thickness, leveling system and rubber mallet for placing the tiles gently and easily.Size of Tile 800 x 800 mm | 480 | sqm |  | 0
22 | Providing and laying Polished Granite stone flooring in required design and patterns, in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry and pointing with white cement slurry admixed with pigment of matching shade including rubbing, curing and polishing etc. all complete as specified and asdirected by the Engineer-in-Charge.a) Polished Granite stone slab colour of Black, Cherry/Ruby Red or equivalent | 3750 | sqm |  | 0
23 | 12 mm cement plaster of mix :1:6 (1 Cement : 6 Manufactured sand) | 1373 | sqm |  | 0
24 | 15 mm cement plaster on the rough side of single or half brick wall of mix :1:6 (1 Cement : 6 Manufactured sand) | 1373 | sqm |  | 0
25 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade:a) New work (Two or more coats applied @ 1.43 ltr/10 sqm over and including priming coat of exterior primer applied 2.20 kg/10 sqm) | 141 | sqm |  | 0
26 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour.Two coats | 100 | sqm |  | 0
27 | Applying priming coats with primer of approved brand and manufacture, having low VOC (Volatile Organic Compound ) content. With water thinnable cement primer on wall surface having VOC content less than 50 grams/litre | 100 | sqm |  | 0
28 | Dismantling Wash Basins,urinals, water closets and other sanitary fixtures including disposal of dismantled materials i/c malba all complete as per directions of Engineer-in-Charge. | 61 | each |  | 0
29 | Dismantling 15 to 40 mm dia G.I. pipe including stacking of dismantled pipes (within 50 metres lead) as per direction of Engineer-in-Charge.(a) Internal Work- Exposed on wall | 195 | metre |  | 0
30 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | 5 | cum |  | 0
31 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer-in-charge. | 77 | sqm |  | 0
32 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.A) In cement mortar | 150 | cum |  | 0
33 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :a) Of area 3 sq. metres and below | 14 | Each |  | 0
34 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :a) Of area beyond 3 sq. metres | 5 | Each |  | 0
35 | Dismantling steel work manually/ by mechanical means in built up sections without dismembering and stacking within 50 metres lead as per direction of Engineer-in-charge. | 2091 | kg |  | 0
36 | Dismantling stone slab flooring laid in cement mortar including stacking of serviceable material and disposal of unserviceable material outside Airport premises and for all leads. | 2921 | sqm |  | 0
37 | Dismantling manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge :a) bituminous road | 250 | sqm |  | 0
38 | Dismantling G.I. pipes (external work) including excavation and refilling trenches after taking out the pipes, manually/ by mechanical means including stacking of pipes within 50 metres lead as per direction of Engineer-in charge :a) 15 mm to 40 mm nominal bore | 50 | metre |  | 0
39 | Dismantling C.I. pipes including excavation and refilling trenches after taking out the pipes, manually/ by mechanical means breaking lead caulked joints, melting of lead and making into blocks including stacking of pipes & lead at site within 50 metre lead as per directionof Engineer-in-charge:a) Up to 150 mm diameter | 145 | metre |  | 0
40 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials outside Airport premises and for all leads. | 10 | each |  | 0
41 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in charge. | 7882 | sqm |  | 0
42 | Painting road surface marking with adequate no. of coats to give uniform finish with ready mixed road marking paint conforming to IS : 164, on bituminous surface/ PQC in white / yellow shade including cleaning the surface of all dirt, scales, oil, grease and foreign material etc. complete. New work (Two or more coats) | 30 | sqm |  | 0
43 | Providing, laying and making kerb channel 30 cm wide and 50 mm thick with cement concrete 1:3:6 (1 cement: 3 coarse sand:6 graded stone aggregate 20 mm nominal size) over 75mm bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including finishing the top smooth etc. complete and as per direction of Engineer-in-charge. | 31 | sqm |  | 0
44 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including excavation ,making drainage opening wherever required complete etc. as per direction of Engineer-in charge (length of finished kerb edging shall be measured for payment).(Precast C.C. kerb stone shall be approved by Engineer-in-charge). | 11 | cum |  | 0
45 | Construction of granular sub-base by providing close graded Material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads & lifts, spreading uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. With material conforming to Grade-I (size range 75 mm to 0.075 mm) having CBR Value-30 | 263 | cum |  | 0
46 | Providing, laying, spreading and compacting graded stone aggregate (size range 53 mm to 0.075 mm ) to wet mix macadam (WMM) specification including premixing the material with water at OMC inmechanical mix plant carriage of mixed material by tipper to site,for all leads & lifts, laying in uniform layers with mechanical paver finisher in sub- base / base course on well prepared surface and compacting with vibratory roller of 8 to 10 ton capacity to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. | 158 | cum |  | 0
47 | Providing and fixing toilet paper holder :C.P. brass | 11 | each |  | 0
48 | Providing and fixing soil, waste and vent pipes :100 mm dia. Hubless centrifugally cast (spun) iron pipes epoxy coated inside & outside IS:15905 | 150 | metre |  | 0
49 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors :100 mm inlet and 100 mm outletHubless centrifugally cast (spun) iron epoxy coated inside & outside as per IS:15905 | 21 | each |  | 0
50 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe withclamps at 1.00 m spacin This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.Internal work - Exposed on wall25 mm nominal dia Pipes | 50 | metre |  | 0
51 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe withclamps at 1.00 m spacin This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.Internal work - Exposed on wall32 mm nominal dia Pipes | 50 | metre |  | 0
52 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge.Conceale work, including cutting chases and making good the walls etc.15 mm nominal dia Pipes | 100 | metre |  | 0
53 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. Thi includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge.Concealed work, including cutting chases and making good the walls etc.20 mm nominal dia Pipes | 50 | metre |  | 0
54 | Providing and fixing square-mouth S.W. gully trap class SP-1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.5 kg and frame to be not less than 2.70 kg as per standard design:100x100 mm size P typeWith F.P.S. (non modular) Fly Ash bricks of class designation 7.5 | 3 | each |  | 0
55 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete :300 mm dia. R.C.C. pipe | 100 | metre |  | 0
56 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 Manufactured sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 Manufactured sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 Manufactured sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 Manufactured sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 Manufactured sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cov 23 kg and weight of frame 15 kg) : With F.P.S. (non modular) Fly ash bricks of class designation 7.5 | 4 | each |  | 0
57 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete :For pipes 100 to 250 mm diameter | 2 | nos |  | 0
58 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) :For fixed portionPolyester powder coated aluminum (minimum thickness of polyester powder coating 50 micron). | 4150 | kg |  | 0
59 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge (Cost of aluminium snap beading shall be paid in basic item):a) With float glass panes of 5 mm thickness (weight not less than 12.50 kg/sqm) | 100 | sqm |  | 0
60 | Providing and fixing 12mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & double acting hydraulic floor spring type fixing arrangeme and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer in charge. | 10 | sqm |  | 0
61 | Providing and laying water proofing treatment to vertical and horizontal surfaces of depressed portions of W.C., kitchen and the like consisting of:(i) Ist course of applying cement slurry @ 4.4 kg/sqm mixed with water proofing compound conforming to IS 2645 in recommended proportions including rounding off junction of vertical and horizontal surface.(ii) IInd course of 20 mm cement plaster 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound in recommended proportion including rounding off junction of vertical and horizontal surface.(iii) IIIrd course of applying blown or residual bitumen applied hot at 1.7 kg. per sqm of area.(iv) IVt course of 400 micron thick PVC sheet. (Overlaps at joints of PVC sheet should be 100 mm wide and pasted to each other with bitumen @ 1.7 kg/sqm). | 150 | sqm |  | 0
62 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. (The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 15750 | kg |  | 0
63 | Designing, Providing, fabricating, testing, protection, installing and fixing in position semi (grid) unitized system of structural glazing (with open joints) for linear as well as curvilinear portions of the building for all heights and all levels, including :a) Structural analysis & design and preparation of shop drawings for the specified design loads conforming to IS 875 part III (the system must passed the proof test at 1.5 times design wind pressur without any failure), including functional design of the aluminium sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and splice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazard including: b Fabricating and supplying serrated M.S. hot dip galvanised / aluminium alloy of 6005 T5 brackets of required sizes, sections and profiles etc. to accommodate 3 Dimensional movement for achieving perfect verticality and fixing structural glazing system rigidly to the RCC/ masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon separator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers.. c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with th structural silicone sealant of required bite size in a clean and controlled factory / work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture, per the approved sealant design, within and all around the perimeter for holding glass d) Providing and fixing in position flashings of solid aluminium sheet 1 mm thick and of sizes, shapes and profiles, as required as per t site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertight. e) Making provision for drainage of moisture/ water that enters the curtain glazing system to make it watertight, by incorporating principles of pressure equalization, providing suitable gutter profiles at bottom (if required), making necessary holes of required sizes and of required numbers etc. complete. This item includes cost of all inputs of designing, labour for fabricating and installation of aluminium grid, installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dul approved by Engineer-in-charge. Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves) on the external face shall be measured in sqm. up to two decimal places.Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accredited by NABL(National Accreditation Board for Testing and Calibration Laboratories),Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories 1. Performance Laboratory Test for Air Leakage Tes 50pa to –300pa) & (+50pa to +300pa) as per ASTM E-283-04 testing method for a range of testing limit 1 to 200 mVhr”.2. Static Water Penetration Test. (50pa to 1500pa) as per ASTME- 331-09 testing method for a range up to 2000 ml.”3. Dynamic Water Penetration (50pa to 1500pa) as per AAMA 501.01- 05 testing method for a range upto 2000 ml”4. Structural Performance Deflection and deformation by static air pressure test (1.5 times design wind pressure without any failure) as per ASTME-330-10 testing method for a range upto 50 mm”5. Seismic Movement Test (upto 30 mm) as per AAMA 501.4-09 testing method for Qualitative test” Tests to be conducted on site6. Onsite Test for Water Leakage for a pressure range 50 kPa to 240 kPa (35psi) upto 2000ml” | 500 | sqm |  | 0
64 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction and of approved size and design/ shape laid in required colour and pattern over and including 50mm thick compacted bed of course sand, filling the joints with fine sand etc. Pavers without edge to be packed with cement mortar in order to hold sand bed all complete per the direction of Engineer-in-charge. | 154 | sqm |  | 0
65 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8mm having water absorption less than 0.5% and conforming to IS: 15622, of approved make in all colours and shades in outdoor floors such as footpath, court yard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 Manufactured sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge. | 45 | sqm |  | 0
66 | Providing and fixing Toilet cubicles with door, pilaster and divider of 18mm thick board both side decorative compact laminate of required colour ,shade and sizes as manufactured as per approved make, including stainless steel accessories ( SS-304 grade) like square top rail. Front panel and divider wall with stripe shoe touching floor (No gap shall be at bottom of divider/front panel except door), knob, thumb turn and indicator, twin coat hook, door stopper, adjustable shoe, gravity hinges, and locking arrangement, SS channel etc as desired. all complete as per drawings. The cubical unit shall be installed in approved finish, shades and colours as per specifications and direction of Engineer in charge. The cubical unit shall be minimum 5 years guarantee for the board against any moisture and 5 years guarantee for the hardwares. L-shape toilet cubicles of size 900m (width) X 1500mm (depth) X 2100mm (height) with door ,External Laminate finish in Metallic shade | 18 | each |  | 0
67 | Providing & fixing white vitreous china wall hung type European type water closet including push fit type pan connector with C.P. bolts, nuts, C.I. chair or other hanging arrangement, with white solid plastic seat and cover with lid, C.P. brass hinge rubber buffers, with accessories,C.I/M.S. brackets painted with two coats of enamel paint of approved shade over a coat of primer. C.P. brass screws and wooden cleats, including cutting and making good the wall and floors wherever required Make: (Kohler 18131IN-S-0), (Hindware Enigma Slim 92502), (Jaquar : SLS-WHT-6951) | 16 | each |  | 0
68 | Providing and Fixing Concealed in wall Flushing Cistern with dual flush Actuator Plate (plastic body in approved finish), flush-stop function, noise less float valve and fast filling action with all component parts of high qualit including fixing frame and set complete in all respects as per direction of the engineer-in-charge Make: (Kohler 77027IN-P-NA + 5413IN-P-CP), (Hindware Concealo), (Jaquar JCS-WHT-2400S) | 10 | each |  | 0
69 | Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100 mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlleddevice (handle lever) conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required:a) White Vitreous china Orissa pattern W.C. pan of size 580x440 mm with integral type foot rests | 2 | each |  | 0
70 | Providing and Fixing vitreous china urinal with C.I. hangers, 15mm dia inlet to built in spreaders with inbuilt waste with C.P flange, complete including cutting and making good the walls and floors wherever required Make: (Kohler Cat No: 5017IN-ER-0), (Hindware Senso art 60018), Jaquar URS-WHT-132530) | 6 | each |  | 0
71 | Providing & fixing Urinal Modesty Panels made of 12 mm thick compact laminated board as per approved make of approved texture/shade having standard dimension of 1200 mm Height x 450 -500 mm Width and made a per IS 2046 (Indian Standard) and as per fire retardant BS-476/97 standard and should be heat, bacteria, water, chemical, scratch and impact resistant . The product should have Green Guard Certificate.Including all accessories as per approval and direction of Engineer-in-Charge .Modesty panels will be fixed to the wall at an height of 500-600mm from the floor with 304 garde SS right angle bracket, 304 grade SS Screws with satin fini & Wall Plugs .The work includes all accessories, machineries, tools etc., complete as per direction of Engineer-in-charge. | 6 | each |  | 0
72 | Providing and Fixing electrical/battery operated concealed automatic flushing system for urinals, including front S.S plate 125 x 125mm chrome sensor with CP brass body, ball valve etc,complete in all respect including cutting and making good the walls wherever required Make: (Kohler 8791T-C01-CP), (Hindware 500964), Jaquar SNR-CHR-51097) | 6 | each |  | 0
73 | Providing and Fixing white vitreous china floor mounted European type water closet including exposed cistern & Pan connector,Flat Back wash basin with one pair of mounting brackets , complete with fittings and seat cover, two no hinged rail 76 cms and five nos of grab bar 60 cms for Handicaped Toilet complete in all respest as per direction of the engineer-in-charge. | 1 | each |  | 0
74 | Providing and Fixing 15 mm nominal bore CP Brass two way bib cock complete wherever required Make: (Hindware), (Jaquar), (CERA) | 13 | each |  | 0
75 | Providing and fixing Health faucet with 1 metre long Flexible Tube and CP wall hook with PVC & SS Screws including cutting and making good the wall wherever required complete as directed by the Engineer-in-charge. | 13 | each |  | 0
76 | Providing and fixing counters (Reception ,Wash basin or other similar locations) with 12 mm thick antibacterial anti fungal, boiling water resistant heat resistant, impact resistant, insulative non conductive, stain resistan scratch resistant, Green Guard certified 100% Acrylic solid surface of approved make ( LG Himac , Dupont, Neonnex , Hanex or equivalent as approved) in approved colour and design, confirming to relevant standards, and having minimum Specific Gravity 1.65 g/cm3, fixed over MS supporting structure with all mechanical fixtures as per manufacturer's specification and guideline, including fascia and back splash area as per approved drawings and design, including fixing of solid acrylic surface over 12 mm thick (BWP) with suitable Low VOC adhesive, moulding of edges, buffing of surface, making of holes for plumbing fixtures, flushing of joints, necessar hardware, silicon sealants, etc. all complete as per direction of Engineer In charge. The plan and elevation area (horizontal and vertical) will be measured for payment. ( No deduction for wash basin area shall be made). | 35 | sqm |  | 0
77 | Providing and fixing automatic sensor faucet for cold water, for wash basin complete in all respect including basin mounted auto tap, with infrared sensors with solenoid valves for cold water with electronic circui and necessary accessories including cutting and making good the walls and floors as per requirement and as per approved manufacturer’s make or equivalent Make: (Kohler Cat No: 18057IN-ND-CP), (Hindware F240001), (Jaquar SNR-CHR-51021) | 20 | each |  | 0
78 | Providing and fixing SS liquid soap dispenser with push lever assembly with soap refill fixed in wall with Screws complete in all respect as per direction of the engineer-in-chargeMake: (Kohler Cat No:5487K-CP), (EURONIC ES-09), (Jaquar ACN-CHR-1137N) | 18 | each |  | 0
79 | Providing and fixing 6mm thick bevelled edge mirror of superior glass in required size and shape of approved quality and approved make complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. bras screws and washers complete at all levels as per detailed drawings and direction of Engineer in Charge. | 13 | each |  | 0
80 | Providing, making and placing in position Check-in counters made up from 19mm thick block board covered with 1.00mm thick laminate of approved make/ shade having hard wood base of specified section including fixin of 12mm thick acrylic polymer solid surface of corian (LG Himac, Dupoint, Neonnex , Hanex or equivalent as approved) at the designated location with necessary fixtures ,fittings etc. complete as shown in the drawing and per the direction of the Engineer-In-Charge. | 25 | each |  | 0
81 | Providing and fixing stainless steel ( Grade 304) railing / frame work made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the sa with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist sl with suitable arrangement as per approval of Engineer-in-charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as fasteners etc.). | 800 | kg |  | 0
82 | Providing, fabricating, testing, installing and fixing in position aluminum Composite Panel Cladding around the columns / dead walls / edges of roof / under side of ceiling / facia etc, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including:Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design. Providing, fabricating and supply and fixing panel of aluminum composite panel cladding in metallic colour of approved shades made out of (5XXX series, H-24 BARE aluminum coil temper) - 4mm thick aluminum composite panel (0.5mm+3mm+0.5mm) material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminum sheets coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin (Minimum70% of resin) coating of approved colour and shade on face # 1( Pencil hardness EN 13523-2 is HB-F) and polymer (Service) coating on face # 2 as specified. Stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc. “weather silicone sealant, backer rods etc.The weight of panel should be minimum 7.5 kg/sqm. The ACP product must conform to EN 13501 class b, s1, d0 with a FPC certification from the Authorized agency. The finished surface shall be be protected with a self-adhesive (rubber based) peel off foil with 70 microns thickness white or black,tested to withstand upto 6 months exposure to loacal weather condition without losing the original pell off characteristics or causing stain or other damages on the coated surface of the aluminium composite panel. The fastening brackets of aluminum alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labou component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminum composite panel cladding, cleaning and protection of the curtain wall with aluminum composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminum items The Contractor shall provide curtain wall with aluminum composite panel cladding, having all the performance characteristics all complete , as per the Architectural drawings, as per item description, specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places." | 951.5 | sqm |  | 0
83 | "Providing and fixing U Baffle Aluminum panel ceiling as per approved make of approved RAL colour consisting of panel size 100 mm deep X 50 mm width using minimum 0.6 mm thick aluminum and 250mm center to center as per drawings enclosed , Pure Polyester Powder Coated, Aluminum alloy AA 3105 (Al. Mg) for higher strength . Panels shall be connected using friction grip upper and lower bracket on a special carrier of 30 mm wide x 30 mm high x 2 mm thick powder coated GI member as approved colour to form as cassette based on the module of 250mm c/c which shall be downward accessible with a torsion springs/ or special bolted bracket hanger system in group of panel or as desired. Main Runners: All vertical baffles are attached to factory punched 30x30x2.0mm Thk black Powder coated G.I member with the special baffle hangers/springs to form a modu of 250mm C/C. Cross Runners: 30 mm wide x 30 mm high x 2 mm thick powder coated GI member as approved colour designed to interlock baffle section on designated spacing are spaced at 1200mm Center maximum. Suspension System : The complete frame to be suspended using special bracket with M6 threaded rod as desired length or as per detailed drawings . Metal baffle ceiling panels according to EN 13964 and quality standar of TAIM/ Green pro e.V.: latest version. Paint Finish: All baffles to be Pure Polyester Powder Coated to RAL Shades as confirmed/approved by Engineer-in-charge. The panels shall be fixed to pre installed structural M.S.frame / RCC work at all levels including all accessories like Fasteners, Hangers, screws, washers, etc at site complete with all respect as desired . conforming to specifications and directions of Engineer-in-Charge .Contractor shall give 10 years guarantee for entire system including Pure Polyester Powder Coating.The Items includes supplying, Installation and fixing of U Baffle Aluminum panel ceiling over MS structural frame / RCC work, Labours, Scaffolding all required machineries for fixing tools, Fasteners, Hangers, screws, washers, etc complete in all respect as desired. ( M.S. structurer/ frame work shall be paid seprately under relevant item ) | 50 | sqm |  | 0
84 | Providing and fixing C.P. brass angle valve of approved quality conforming to IS:893115mm nominal bore Make: (Kohler Cat No: 80154IN-4-CP), (Hindware Cat No: F310003), (Jaquar FLR-CHR-5053N) | 13 | each |  | 0
85 | Providing and fixing GI Clip in Metal Ceiling System of 600x600/ 600x1200 mm module at all height which includes providing and fixing ‘C’ wall angle of size 20x30x20 mm made of 0.5 mm thick pre painted steel along the perimeter of the room with help of nylon sleeves and wooden screws at 300 mm center to centre, suspending the main C carrier of size 10x38x10 mm made of G.I steel 0.7 mm thick from the soffit with help of soffit cleat 37x27x25x1.6 mm, rawl plugs of size 38x12 mm and C carrier suspension clip and main carrier bracket at 1000 mm c/c. Inverted triangle shaped Spring Tee having height of 24 mm and width of 34 mm made of GI steel 0.4 mm thick is then fixed to the main C carrier and in direction perpendicular to it at 600 mm centers with help of suspension brackets. Wherever the main C carrier and spring T have to join, C carrier and spring T connectors have to be used. All sections to be galvanized @ 120 gms/sqm (both side inclusive),fixing with clip in tiles into spring ‘T’ with GI Metal Ceiling Clip in plain Beveled edge global white color tiles of size 600x600/600x1200 an 0.5 mm thick with 25 mm height, made of G I sheet having galvanizing of 100 gms/ sqm (both sides inclusive) and 20% perforation area with 1.8 mm dia holes and having NRC of 0.5, electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending and perforation . | 3200 | sqm |  | 0
86 | Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as per IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with 6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the spacing of 1200 mm centre to centre, to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high having flanges o 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @ 230 mm interval, including fixing of gypsum board to ceiling section and perimeter channel with the help of dry wall screws of size 3.5 x 25 mm at 230 mm c/c, including jointing and finishing to a flush finish of tapered and square edges of the board with recommended jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm on both sides of joint and two coats of primer suitable for board, all as per manufacturer’s specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge but excluding the cost of painting with12.5mm thick tapered edge gypsum plain board conforming to IS: 2095- Part I | 125 | sqm |  | 0
87 | Providing and Fixing SS Grating with frame and SS Screws casted heavy 125 mm dia complete as directed by Engineer-in-charge. | 21 | each |  | 0
88 | Providing and fixing 32mm CP Brass Bottle Trap of approved quality & make and as per the direction of Engineering- charge Make: (Kohler Cat No: 7314IN-CP), (Hindware F850015), (Jaquar ALD CHR-769L300X190) | 13 | each |  | 0
89 | Fabrication, supply & installation of Floor mounted SS-316 grade glass railing made up of 50mm dia top rail mounted on SS soild flat baluster of 54x12mm width to hold the top rail, Height of the railing shall be 1200mm from the floor to the top of the top rail,The baluster shall have infill of 10.89mm thick ( 5+0.89 SGP+5) laminated Toughened glass with height of 800mm high and length as per the layout plan connected to the baluster w SS 304 grade Glass holders.The balusters shall be mounted on the floor with SS Grade 304 base plate of 100x 100mm x 8mm thick fixed on the floor with 4 No. M-8 grade GI threaded chemically grouted SS-304 grade fasteners.The work shall be done upto the satisfaction of the Engineer-in-Charge. (Please note that no welding of SS pipes will be allowed and work shall be done by a specialized agency on modular and component basis). | 50 | metre |  | 0
90 | Providing, Fabricating and installation in position of Security check for ladies (Frisking Booth ) comprising frame work of SS Section 50 x 50x 3mm over the 12mm thick M.S base Plate fixed to the floor with the help of the fasteners.The frame work is covered with 12mm thick Toughened Glass screwed to the SS frame work with the help of 25 dia SS studs,the toughened glass shall have 3 mm thick fasara film Matte crystal ( SH2 MACRX ) patsed internally, the frisking booth shall be a complete unit in itself with all necessary fittings, fixtures etc.complete as shown in the drawing and as per the direction of the Engineer-In-Charge. | 4 | each |  | 0
91 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineerin-charge.a) Pre-laminated particle board with decorative lamination on one side and balancing lamination on other side | 48 | sqm |  | 0
92 | Providing and fixing frame work for partitions/ wall lining etc. made of 50x50x1.6 mm hollow MS tube, angle , MS plate, Placed along the walls, ceiling and floor in a grid pattern with spacing as per drawing both ways (vertically & horizontally) or at required spacing near opening, with necessary welding at junctions and fixing the frame to wall/ ceiling/ floors with steel dash fasteners of 8 mm dia, 75 mm long bolt, including making provision for opening for doors, windows, electrical conduits, switch boards etc. Including providing with two coats of approved steel primer etc. complete, all as per direction of Engineer-in-charge. | 1000 | kg |  | 0
93 | Tensile fabric roofing - PVC COATED FABRICFabric patterning, Supply, Fabrication && Installation of Serge Ferrari Type 2 of apy Colour 900 GSM Fabric for covering MS structure at Pune AAI (Include: Material: Serge Ferra Fabric Type 2, with 10 years waranty from manufacturerer, Membrane Plate, Wireropes, Nut Bolts, Ites Require Accessories, Aluminium Section, Sda Screw, SS. 316 GradeTerminal, Service: Supply, Transport, etc) Rate includes Purchasing of fabric (including Cost, Insurance and Freight, Taxes etc), shop drawings. Fabrication (including Cutting and High frequency welding to obtain the form), Transport to the site, assembling, Installation etc. complete as per direction of Engineer-In charge & nothing extra shall be paid. | 120 | sqm |  | 0
94 | Dismantling stainless steel work including dismembering and stacking within 50 metres lead. | 1046 | kg |  | 0
95 | Dismantling existing toilet cubicles (including doors) including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge. | 10 | each |  | 0
96 | Dismantling of Aluminium grill in various locations including stacking of useful materials near the site and disposal of unserviceable materials outside Airport premises and for all leads. | 238 | sqm |  | 0
97 | Providing & Fixing of Fixed Glass Partitions with 12mm Clear Toughened Glass including all fixtures and fittings of approved make all complete as per direction of Engineer in charge. | 50 | sqm |  | 0
98 | Designing,Providing, assembling and supplying vision glass panels (IGUs) comprising of hermetically-sealed 37.52mm thick Insulated glass comprising of 13.52mm Thick Heat Strengthened (HS) Laminated Outerlite (6mm thick Clear Heat Strengthened glass + 1.52 structural Interlayer SGP + 6mm thick Heat Strengthened Performance glass) + 16mm Air Space Gap + 8mm Thick Clear Heat Soaked toughened Innerlite glass , of approved colour and shade with reflective soft / hard coating on surface # 2 , dessicants, including primary seal and secondary seal (structural silicone sealant) etc. all complete for the required performances, as per the Architectur drawings, as per the approved shop drawings, as specified and as directed by the Engineer-in-Charge. The IGUs shall be assembled in the factory/ workshop of the glass processor.“(Payment for fixing of IGU Panels in the curtain glazing is included in cost of under respective item )“For payment, only the actual area of glass on face # 1 of the glass panels (including the areas of the grooves and weather silicone sealant)provided and fixed in position, shall be measured in sqm.“.(i) Glass - 37.52mm thick Insulated glass comprising of 13.52mm Thick Heat Strengthened (HS) Laminated Outerlite (6mm thick Clear Heat Strengthened glass + 1.52 structural Interlayer SGP + 6mm thick Heat Strengthened Performance glass) + 16mm Air Space Gap + 8mm Thick Clear Heat Soaked toughened Innerlite glass (properties as visible Light transmittance (VLT) 39%, Light reflection internal 10 to 22%, light reflection external 10 to 22 %, SHGC less than or equal to 0.24 and U value of less than 1.70 W/m2 degree K etc). | 450 | sqm |  | 0
99 | Extra for openable side / top hung vision glass panels (IGUs) including providing and supplying at site all accessories and hardwares for the openable panels as specified and of the approved make such as heavy duty stainless steel friction hinges, min 4 -point cremone locking sets with stainless steel plates, handles, buffers etc. including necessary stainless steel screws/ fasteners, nuts, bolts, washers etc. all complete as per the Architectural drawings, as per the approved shop drawings, as specified and as directed by the Engineer- in-Charge. | 10 | sqm |  | 0
100 | Providing and fixing broom finish Stainless steel sheet ( 304 grade) Column / wall Cladding,skirting refer drawing made out of 1.2mm thick Stainless steel sheet of extruded sections, fixing with frame ,screws, rubber beading (for holding screws ) etc. complete with all respect as desired as per drawing and manufacturers specifications and direction of Engineer in charge.( payment shall be paid of actual area of skirting cladding.) | 208 | sqm |  | 0
101 | Providing and fixing 3M™ Scotchal electro cut Dusted /Crystal ( acid -etched look ) 7725SE-314/324 Graphic Film over the designated locations shown in the drawing in any design, colour and pattern or as per the directio of the Engineer-In-Charge. | 200 | sqm |  | 0
102 | Excavation in soil with hydraulic excavator of 0.9 cum bucket capacity including cutting and loading in tippers, trimming bottom and side slopes, in accordance with requirements of lines, grades and cross sections, and transporting to the embankment location (outside Airport premises) with all lifts and lead. | 560 | cum |  | 0
103 | Excavation in hard rock (blasting prohibited) with rock breakers including breaking rock, loading in tippers and disposal to the embankment location within all lifts and lead (Airport operational premises), trimming botto and side slopes in accordance with requirements of lines, grades and cross sections. | 280 | cum |  | 0
104 | Filling available excavated earth in the airport operational premises including all leads etc. complete (Excluding rock) in embankments, depressions etc. in accordance with requirements of lines, grades and cross sections in layers not exceeding 20cm in depth, consolidating each deposited layer by watering & ramming and every 3rd & topmost layer with 8-10 Tonne Vibratory roller, etc complete as per direction of Engineer-in-charge. | 112 | cum |  | 0
105 | Providing and applying primer coat with bitumen emulsion SS1 grade conforming to IS:8887 on prepared surface of Granular Base including clearing of surface and spraying primer at the rate of 0.70 kg/sqm using mechanical means complete in all respects as per direction of Engineer-In-Charge. The contractor shall quote his rates assuming quantity of bitumen emulsion as 0.70 Kg/Sqm. If the actual quantity of bitumen emulsion varies from the quantity assumed above, necessary cost adjustment for deviation in the quantity of bitumen emulsion shall be done as per rate in actual supply voucher from nearest refinery at the time of execution. The rate of bitumen emulsion exclusive of GST shall only be considered for payment. | 1050 | sqm |  | 0
106 | Providing and applying tack coat using suitable low viscosity paving bitumen of VG 10 grade conforming to IS:73 spraying the bitumen with mechanically operated spray unit at the rate specified below, cleaning and preparing the existing pavement surface as per specifications complete in all respects as per direction of Engineer-In-Charge. If the actual quantity of bitumen varies from the quantity specified, necessary cost adjustment for deviation in the quantity of bitumen shall be done as per rate in actual supply voucher from nearest refinery at the time of execution. The rate of bitumen exclusive of GST shall only be considered for payment.a) 0.20 Kg/Sqm on existing bituminous surface | 1050 | sqm |  | 0
107 | Providing and laying of Hot Mix Dense Bituminous Macadam (DBM) using crushed stone aggregate of quality, size and grading as specified and filler (hydrated lime) and Viscosity Grade Bitumen (supplied in bulk) in proportions as per job mix formula and laid to specified levels, grade and camber as per specification, drawings and as directed by the Engineer-in-Charge including compacting with 8-10 tonne, preferably vibratory road roller of adequate capacity to achieve the specified values of compaction, strength, surface accuracy complete [for tendering purpose VG bitumen of grade VG-30 shall be taken as 110 kg/m3 of mix supplied in bulk produced by Govt. Refineries and 2% hydrated lime by weight of aggregates as filler material].The necessary cost adjustment shall be made based on JMF & availability of filler. | 53 | cum |  | 0
108 | Providing and laying of Hot Mix Semi Dense Asphaltic Concrete (SDAC) using crushed stone aggregate of quality, size and grading as specified and filler (hydrated lime) and Viscosity Grade Bitumen (supplied in bulk) in proportions as per job mix formula and laid to specified levels, grade and camber as per specification, drawings and as directed by the Engineer-in-Charge including compacting with 8-10 tonne, preferably vibratory road roller of adequate capacity to achieve the specified values of compaction, strength, surface accuracy complete [for tendering purpose VG bitumen of grade VG-30 content shall be taken as 120 kg/m3 of mix supplied in bulk produced by Govt. Refineries and 2% hydrated lime by weight of aggregates as filler material].The necessary cost adjustment shall be made based on JMF & availability of filler. | 53 | cum |  | 0
109 | Providing and fixing profile 1.2mm thick TCT colour coated galvanized steel as per approved make having minimum 240-245MPa yield strength as per IS 513 with a crest height of 44 to 51 at a pitch distance of 130 to 316mm c/c having a cover width of 760 to 960mm. The galvanization shall be minimum 275 gm per sqcm as per IS 277 with colour coating of polyester quality paint of 20 microns over the primer coat of 5 microns on th exposed side and 5 microns alkyde coat over 5 microns primer coat on the inner side/ hot dipped zinc coating of 275 gm/sqcm on both sides confirming to AS 1397 and BS EN 10147:2000 complete the job with all respect as desired and as per the direction of Engineer-incharge. | 183 | sqm |  | 0
110 | Providing Consultancy services for MEP works including planning,designing etc. as per direction of E-I-C and as per scope of work given in technical specification (Electrical) | 1 | Job |  | 0
111 | Credit for taking away Serviceable bricks outside AAI premises as per direction of Engineer In charge | 1108 | nos. |  | 0
112 | Credit for taking away serviceable false ceiling outside AAI premises as per direction of EIC | 930 | kg |  | 0
113 | Credit for taking away serviceable wooden doors outside AAI premises as per direction of EIC | 2 | each |  | 0
114 | Credit for taking away serviceable Aluminium outside AAI premises as per direction of EIC | 3131 | kg |  | 0
115 | Credit for taking away serviceable glass outside AAI premises as per direction of EIC | 3319 | sqm |  | 0
116 | Credit for taking away serviceable steel reinforcement outside AAI premises as per direction of EIC | 330 | kg |  | 0
117 | Credit for taking away serviceable Stainless Steel outside AAI premises as per direction of EIC | 729 | kg |  | 0
118 | Credit for taking away Steel dismantled from window, door frame, any existing steel structure etc. outside AAI premises as per direction of EIC | 1152 | kg |  | 0
119 | Credit for taking away dismantled pillar cock, bib cock, bottle trap etc. outside AAI premises as per direction of EIC | 100 | kg |  | 0
120 | Cartage of malba by tractor trolley from inside AAI premises to out side AAI premises upto a distance of 5 km by mechanical means including loading and unloading complete as desired by the Engineer-in-charge | 50 | per trip |  | 0
121 | SH II - Electrical Works
122 | Panel 1: Design, fabrication, assembly, wiring and supply, erection, testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hz system suitable for a symmetrical fault level of 36 kA at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5 sq.mm & 2.5sq.mm for CT's etc. paint finish of approved shade over metal surface cleaned and treated with seven tank process complete with interconnections etc. as per specifications, as complete as required as per specifications and drawing attached. Mechanical interlock between incomers and bus coupler to be provided. Incomer- (a) 2 nos 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link, (b) R,Y,B indication lamp- 2 Set (c) ON, OFF, TRIP indication lamp- 02 Sets, (d) 2A SP 10kA control MCB (e) Digital multifunction meter with suitable ratio CTs of class 1.0 accuracy - 02 sets. Bus-coupler: (a) 01 No. 400 A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link etc. (b) ON, OFF, TRIP indication lamp- 01 Set (c) 2A SP 10kA control MCB Outgoing: (a) 200 A- 02 Nos, 160 A - 02 Nos, 100 A - 04 Nos and 63 A- 12 Nos (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link (b) ON, OFF, TRIP indication lamp- 20 Set (e) All outgoings shall have RYB indication LED lamp with 2A SP MCB control . Busbar : TPN Aluminium alloy bus bars for high conductivity - 400A Rating, Isc=36kA for 1 sec | 1 | Job |  | 0
123 | Panel 2: Design, fabrication, assembly, wiring and supply, erection, testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hz system suitable for a symmetrical fault level of 36 kA at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5 sq.mm & 2.5sq.mm for CT's etc. paint finish of approved shade over metal surface cleaned and treated with seven tank process complete with interconnections etc. as per specifications, as complete as required as per specifications and drawing attached. Mechanical interlock between incomers and bus coupler to be provided. Incomer- (a) 2 nos 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link, (b) R,Y,B indication lamp- 2 Set (c) ON, OFF, TRIP indication lamp- 02 Sets, (d) 2A SP 10kA control MCB (e) Digital multifunction meter with suitable ratio CTs of class 1.0 accuracy - 02 sets. Bus-coupler: (a) 01 No. 400 A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link etc. (b) ON, OFF, TRIP indication lamp- 01 Set (c) 2A SP 10kA control MCB Outgoing: (a) 200 A- 02 Nos, and 63 A- 14 Nos (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link (b) ON, OFF, TRIP indication lamp- 16 Set (c) All outgoings shall have RYB indication LED lamp with 2A SP MCB control . Busbar : TPN Aluminium alloy bus bars for high conductivity - 400A Rating, Isc=36kA for 1 sec | 1 | Job |  | 0
124 | Panel 3: Design, fabrication, assembly, wiring and supply, erection, testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hz system suitable for a symmetrical fault level of 36 kA at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5 sq.mm & 2.5sq.mm for CT's etc. paint finish of approved shade over metal surface cleaned and treated with seven tank process complete with interconnections etc. as per specifications, as complete as required as per specifications and drawing attached. Mechanical interlock between incomers and bus coupler to be provided. Incomer- (a) 1 nos 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link, (b) R,Y,B indication lamp- 1 Set (c) ON, OFF, TRIP indication lamp- 01 Sets, (d) 2A SP 10kA control MCB (e) Digital multifunction meter with suitable ratio CTs of class 1.0 accuracy - 01 sets. Outgoing: (a) 63 A- 6 Nos (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link (b) ON, OFF, TRIP indication lamp- 16 Set (c) All outgoings shall have RYB indication LED lamp with 2A SP MCB control . Busbar : TPN Aluminium alloy bus bars for high conductivity - 400A Rating, Isc=36kA for 1 sec | 1 | Job |  | 0
125 | Panel 4: Design, fabrication, assembly, wiring and supply, erection, testing and commissioning of cubicle type compartmentalised as per Form 4B free standing, dust and vermin proof (Minimum IP 42 ingress protection) front operated switchboards conforming to IS 8623/IEC-60439 suitable for use at 433 volts, 3 phase 4 wire 50 Hz system suitable for a symmetrical fault level of 36 kA at 433 volts, fabricated from 2 mm outer thick CRCA sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top and bottom including lifting hooks and earth bus of required size for prospective fault level at that panel with 2 nos. earthing terminals, coating, required and as below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5 sq.mm & 2.5sq.mm for CT's etc. paint finish of approved shade over metal surface cleaned and treated with seven tank process complete with interconnections etc. as per specifications, as complete as required as per specifications and drawing attached. Mechanical interlock between incomers and bus coupler to be provided. Incomer- (a) 1 nos 400A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link, (b) R,Y,B indication lamp- 1 Set (c) ON, OFF, TRIP indication lamp- 01 Sets, (d) 2A SP 10kA control MCB (e) Digital multifunction meter with suitable ratio CTs of class 1.0 accuracy - 01 sets. Outgoing: (a) 63 A- 12 Nos (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c extended rotary handle, spreader link (b) ON, OFF, TRIP indication lamp- 12 Set (c) All outgoings shall have RYB indication LED lamp with 2A SP MCB control . Busbar : TPN Aluminium alloy bus bars for high conductivity - 400A Rating, Isc=36kA for 1 sec | 2 | Job |  | 0
126 | Supply, Installation, Testing and Commissioningof following rated high performance IGBT based fully microprocessor controlled (three phase Input & three phase Output)online UPS system suitable for input and output parameters as per specifications. The UPS shall have Separate Galvanic Isolation Transformer Inbuilt/External K13 Copper Wound (After Static Switch) transformer. The UPS shall be provided in powder coated fan cooled enclosure painted in colour as per specifications. The UPS shall be suitable for normal, emergency, recharge, by-pass and maintenance mode including bypass arrangement. The UPS shall have a microprocessor base display and control panel. UPS shall have own batteries with 30 minute battery back-up with SMF batteries.Complete system must be provided as per specifications approved drawing and as per site requirement including inter connecting cables from battery to UPS, UPS to panel with single core copper cabling etc. UPS shall work on parallel/ hot redundancy mode, cost of supporting kit shall be included. supports for complete system as approved by the Engineer in charge complete in all respect.
127 | 30 KVA | 2 | Job |  | 0
128 | WIRING WORK - POINT WIRING
129 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable etc. as required. - Group C | 165 | Point |  | 0
130 | Wiring for MCB control primary light point/ fan point/ exhaust fan point/ call bell point with 2.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed steel conduit and earthing the point with 2.5 sq.mm FRLSH PVC insulated copper conductor single core cable etc. as required. - (MCB cost is included in the DB) | 45 | Point |  | 0
131 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLSH PVC insulated copper conductor single core cable etc. as required. - Group C | 360 | Point |  | 0
132 | Wiring for light plug with 2X2.5 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit along with 1 No. 2.5 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 500 | M |  | 0
133 | Wiring for power plug with 2X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed steel conduit along with 1 No. 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 300 | M |  | 0
134 | Wiring for circuit/ submain wiring along with earth wirewith the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
135 | 2 x 1.5 sq. mm + 1 x 1.5 sq. mm earth wire | 1200 | M |  | 0
136 | 2 x 2.5 sq. mm + 1 x 2.5 sq. mm earth wire. | 800 | M |  | 0
137 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire (for industrial sockets and SPNDB ) | 200 | M |  | 0
138 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire (for industrial sockets ) | 200 | M |  | 0
139 | Supply and wiring for circuit/sub main wiring with the following sizes of FRLSH PVC insulated copper conductor unarmoured power cable on existing surface /raceways etc. as required, complaining to IS - 7098 and relevant standards.
140 | 3 x 2.5 sq. mm | 200 | M |  | 0
141 | 3 x 4 sq. mm | 200 | M |  | 0
142 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. (For ELV Services)
143 | 20 mm | 400 | M |  | 0
144 | 25 mm | 500 | M |  | 0
145 | 32 mm | 600 | M |  | 0
146 | Supplying and fixing of following sizes of Heavy class FR PVC (ISI marked) conduitalong with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
147 | 20 mm | 200 | M |  | 0
148 | 25 mm | 250 | M |  | 0
149 | 32 mm | 250 | M |  | 0
150 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | 30 | Nos. |  | 0
151 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 2 Nos. 3 pin 5/6 amps modular socket outlet and 2 Nos. 6 amps modular switch, connection etc. as required. | 30 | Nos. |  | 0
152 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 50 | M |  | 0
153 | Supplying, fixing, testing & commissioning of 32 A, 240 V, SPN Industrial type socket outlet (IP-65), with 2 pole and earth, plug top along with 32 A, “C” curve, SP, MCB, in Polycarbonate enclosure, on surface or in recess, with cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5 | Nos. |  | 0
154 | Supplying fixing, testing & commissioning of 32 A, 415 V, TPN Industrial type socket outlet (IP-65), with 4 pole and earth, plug top along with 32 A, “C” curve, TPMCB, in polycarbonate enclosure, on surface or in recess, with cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5 | Nos. |  | 0
155 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
156 | 5/6 amp switch | 35 | Nos. |  | 0
157 | 15/16 amp switch | 50 | Nos. |  | 0
158 | 3 pin 5/6 amp socket | 35 | Nos. |  | 0
159 | 5 pin 15/16 amp socket | 50 | Nos. |  | 0
160 | Supplying and fixing following size modules, GI box along with modular base & cover plate for modular switches in recess etc. as required.
161 | 1 or 2 Module (75mm X 75mm) | 8 | Nos. |  | 0
162 | 3 Module (100mm X 75mm) | 30 | Nos. |  | 0
163 | 4 Module (125mm X 75mm) | 25 | Nos. |  | 0
164 | 6 Module (200mm X 75mm) | 25 | Nos. |  | 0
165 | 8 Module (200mmX125mm) | 25 | Nos. |  | 0
166 | Supplying and fixing modular blanking plateon the existing modular plate & switch box excluding modular plate as required. | 30 | Nos. |  | 0
167 | DISTRIBUTION BOARDS, MCBs & MCCBs
168 | S/F TPN MCB DB: Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB PPI distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/ Isolator)
169 | 4 way (4 + 6 +12), Double door, horizontal type | 5 | Set |  | 0
170 | 8 way (4 +6+ 24), Double door, horizontal type | 14 | Set |  | 0
171 | S/F prewired SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 12 way, Double door | 10 | Set |  | 0
172 | SITC 4P MCB 'C' Curve: Supplying and fixing following rating, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
173 | 40 amps | 5 | Set |  | 0
174 | 63 amps | 14 | Set |  | 0
175 | SITC 'C' series, SP MCB: Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 480 | Set |  | 0
176 | Supplying and fixing single pole blanking platein the existing MCB DB complete etc. as required. | 16 | Nos. |  | 0
177 | Supplying fixing, testing & commissioning of following rating, double pole, 240 V, 10KA c curve, isolatorin the existing MCB DB complete with connections, testing and commissioning etc. as required.
178 | 40 amps | 10 | Nos. |  | 0
179 | Supplying fixing, testing & commissioning of following rating, double pole, 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
180 | 40 amps | 15 | Nos. |  | 0
181 | 63 amps | 42 | Nos. |  | 0
182 | Supplying, installation, testing & commissioning of Junction boxes for D.B outgoings/ cables, wires etc.complete with interconnection/bus bars & made of same material & finishes as per specifications of DB's.
183 | Cable End box for 4 way TPN DB | 5 | Nos. |  | 0
184 | Cable End box for 6 way TPN DB | 2 | Nos. |  | 0
185 | Cable End box for 8 way TPN DB | 14 | Nos. |  | 0
186 | Cable End box for 12 way TPN DB | 10 | Nos. |  | 0
187 | LIGHTING FIXTURES & ACCESSORIES
188 | INTERNAL LIGHTING FIXTURES SUPPLY & INSTALLATION
189 | Supply, Installation, testing and commissioning of Recess mounted LED 600x600 mm fitting made of zinc-coated steel , fixture should have minimum efficacy at System level (Not Chip Level) >=120lumens/watt, 4000lm, Life of fixture 50000hrs@L70B50 Lumen maintenance, CCT up to 4000, CRI minimum 80, PF >0.95, and an operating Voltage Range of 150 - 270 Internal Surge Protection 2.5KV. LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory.The fixture should comply with the other parameters as per IS10322 and specifications. Minimum system Lumens 4000. | 150 | Nos. |  | 0
190 | Supply, Installation, testing and commissioning of Recess mounted LED Down lighter with a nominal system lumen output of 2200 lumens and a minimum system efficacy of 110 lm/W. The luminaire should have a colour temperature of 4000K and CRI minimum 80. The luminaire shall meet IP20 rating with THD<10% and PF > 0.95. LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory.The luminaire housing should made of die-cast aluminium with a aluminium coated plastic diffuser. The luminaire should have high gloss mirror optics. The fixture should comply with the other parameters as per IS10322 and specifications. | 150 | Nos. |  | 0
191 | Supply, Installation, testing and commissioning of Recess mounted LED Down lighter with a nominal system lumen output of 1200 lumens and a minimum system efficacy of 110 lm/W. The luminaire should have a colour temperature of 4000K and CRI minimum 80. The luminaire shall meet IP20 rating with THD<10% and PF > 0.95.LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory. The luminaire housing should made of die-cast aluminium with a aluminium coated plastic diffuser. The luminaire should have high gloss mirror optics. The fixture should comply with the other parameters as per IS10322 and specifications. | 70 | Nos. |  | 0
192 | Supply, Installation, testing and commissioning of Batten LED 4ft with a nominal system lumen output of 4000 lumens and a minimum system efficacy of 100 lm/W. The luminaire shall have a rated system lifetime of 40,000 burning hours at L70. The luminaire should have a colour temperature of 5700/6500K and CRI minimum 80. The luminaire shall meet IP20 rating with THD < 10% and PF > 0.95.LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory.The luminaire housing should made of CRCA with a PC glossy diffuser. The fixture should comply with the other parameters as per IS10322 and specifications. | 50 | Nos. |  | 0
193 | Supply, Installation, testing and commissioning of Batten LED 4ft with a nominal system lumen output of 2000 lumens and a minimum system efficacy of 100 lm/W. The luminaire shall have a rated system lifetime of 40,000 burning hours at L70. The luminaire should have a colour temperature of 5700/6500K and CRI minimum 80. The luminaire shall meet IP20 rating with THD < 10% and PF > 0.95.LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory.The luminaire housing should made of CRCA with a PC glossy diffuser. The fixture should comply with the other parameters as per IS10322 and specifications. | 20 | Nos. |  | 0
194 | Supply, Installation, testing and commissioning of High Pressure Die Cast Aluminium Alloy housing Medium Bay LED Luminaire of 9000 system lumen specially designed heat sinks dust free. For high ceiling heights having beam Angle 60 deg / 90Degree,PMMA/PC material specialized Lenses for effective light distribution, Luminous flux (Lumen)9000.Corelated Colour Temp 4000k, CRI minimum 70,Maintenance of lumen L70 (Hrs) 50K@L70,Ambient temperature (Ta) 45Degree,optics narrow or wide beam optics, optical cover glass. Aluminium PDC Housing. Protection of Fixture:- IP65,Class I, power factor >0.95, Surge protection 4KV,Votage range 150-270V AC, Lumen standard /Test certificate as per IS10322. The fixture should comply with the other parameters as per IS10322 and specifications. LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory.The fixtures shall be supplied with the painting and finishings similar to the baffles/ceiling colour pattern required at site. (Fixtures shall also be supplied with polycarbonate junction box suitable for loop in loop out of 3x4 sq. mm power cable and suitable wire for automation controls.) | 60 | Nos. |  | 0
195 | Supply, Installation, testing and commissioning of High Pressure Die Cast Aluminium Alloy housing High Bay LED Luminaire of 15000 system lumen specially designed heat sinks dust free. For high ceiling heights having beam Angle 60 deg / 90Degree,PMMA/PC material specialized Lenses for effective light distribution, Luminous flux (Lumen)16500.Corelated Colour Temp 5000/6500k, CRI minimum 70,Maintenance of lumen L70 (Hrs) 50K@L70,Ambient temperature (Ta) 45Degree,optics narrow or wide beam optics, optical cover glass. Aluminium PDC Housing. Protection of Fixture:- IP65,Class I, power factor >0.95, Surge protection 4KV,Votage range 150-270V AC, Lumen standard /Test certificate as per IS10322. LM 79 and LM80 reports needs to be submitted from a NABL/UL Approved Laboratory. The fixture should comply with the other parameters as per IS10322 and specifications. The fixtures shall be supplied with the painting and finishing similar to the baffles/ceiling colour pattern required at site. (Fixtures shall also be supplied with polycarbonate junction box suitable for looping loop out of 3x4 sq. mm power cable and 2x1.5 sq.mm wire for automation controls.) | 50 | Nos. |  | 0
196 | Supply, Installation, testing and commissioning of Linear profiles for cove lighting with Low profile housing height of 21 mm (.86 in), including mounting clips. The housing should be of Extruded polycarbonate, white finish. The lens should be of clear polycarbonate. The luminaire should have options for standalone (1ft/4ft) unit lengths and should also have provision for continuous mounting with 110 degrees beam angle. LED Used shall be SMD type and fixture should have minimum efficacy at System level (Not Chip Level) >=100lumens/watt, Life of fixture 50000hrs@L70B50 Lumen maintenance, CCT choice available in 4000K and 3000K, CRI minimum 80, PF >0.9, THD<10%, an operating Voltage Range of 150 - 270 V, 50Hz. The fixture should comply with the other parameters as per IS10322 and specifications. The luminaire should be suitable to work in damp location, IP40 and IK08 rated. The fixture should comply with the parameters as per IS10322 Minimum system Lumens 1100 for a 4ft luminaire. | 100 | M |  | 0
197 | Supply, Installation, testing and commissioning of 400 mm sweep wall fans complete with double ball bearing, motor, blades, canopies, capacitor etc. suitable for operation on 230 volts, 50 Hz., 1 phase, AC supply complete as required. Wall mounted hanging arrangement including wiring with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable, including providing and fixing phenolic laminated sheet cover on the fan box etc. as required. | 10 | Nos. |  | 0
198 | Supplying, installation, testing and commissioning of Passive Infrared(PIR) technology based occupancy sensor having high performance, non regulating programmable type, suitable for connected load upto 10 A, for mounting height up to 2.8 meter and for 5-7 meter diameter coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required. | 5 | Nos. |  | 0
199 | EXTERNAL ROAD LIGHTING
200 | Supply, assembly, erection, connecting, testing & commissioning of standard 7.0 metre high (above ground) GRP Pole (Pressures as per IS 875 Part-3), with stiffeners, chain, Allen bolt, single arm bracket, foundation bolts, pre fabricated plate, template, accessories, nut and washers, factory finish, Base plate. The column shall also be provided with flush door at the bottom with proper strengthening to the cut-out of the door opening, an outdoor IP-66 rated junction/ looping box with Heavy duty 3 phase & Neutral, 32 Amp connector with 10A DP MCB, double earthing arrangements, including all accessories complete as required as per specifications & approved by the Engineer Incharge. | 3 | Nos. |  | 0
201 | Supply, assembly, erection, connecting, testing & commissioning of standard 7.0 metre high (above ground) GRP Pole (Pressures as per IS 875 Part-3), with stiffeners, chain, Allen bolt, Double arm bracket, foundation bolts, pre fabricated plate, template, accessories, nut and washers, factory finish, Base plate. The column shall also be provided with flush door at the bottom with proper strengthening to the cut-out of the door opening, an outdoor IP-66 rated junction/ looping box with Heavy duty 3 phase & Neutral, 32 Amp connector with 10A DP MCB, double earthing arrangements, including all accessories complete as required as per specifications & approved by the Engineer Incharge. | 3 | Nos. |  | 0
202 | Supply, Installation, testing and commissioning of Epoxy powder coated pressure die-cast aluminium housing with weather-proof gasket for LED including 150 W LED street light sand control gear compartments, frame with heat resistant toughened clear glass fixed with SS screws. Colour temp. – 5700K/6500K with 10kV external surge protector, Input voltage range: 150–270V AC. Side entry mounting for 50 to 60 mm OD pipe bracket.LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory. and other parameters as per IS-10322 and complying to the specifications. | 9 | Nos. |  | 0
203 | Supply Installation, testing and commissioning of 20 M high mast shaft in two sections suitable for wind speed as per specifications, with raising lowering system comprising, head frame, luminaries carriage suitable to install 8 nos luminaries in symmetrical arrangement, double drum winch, 6mm diameter SS wire rope, integral power tool motor, manual handle, trailing cable, connector, integral power tool motor, manual handle, junction box, lightening finial, foundation bolts manufactured from special steel along with nuts, washers, anchor plate including LED type single dome aviation obstruction light including suitable wiring from MCB to fixtures all complete as required per site & approved by engineer-in charge. | 1 | Nos. |  | 0
204 | Supply, installation on 20 M height High Mast pole, testing commissioning of 5700K 350W LED flood light fitting suitable for 230V 1-ph 50Hz AC supply having efficacy ≥110 lumen/watt, burning hours ≥ 50000 Hours, CRI ≥70, THD <10%, high pressure die cast Alminium/standard alloy housing, IP≥65, surge protection >4kV, p.f.≥0.95, driver with efficiency ≥85%, total power consumption <110% of rated capacity of LED fitting,LM 79 and LM 80 reports need to be submitted from a NABL/UL Approved Laboratory, 05 years OEM warranty for entire fitting with driver etcc.omplete as required as directed by Engineer-In-Charge. | 8 | Nos. |  | 0
205 | Supply Installation, testing and commissioning of outdoor stand mounted feeder pillar with 63A TPN MCB incomer, single dial time switch, 45A TP contactor for the automatic switching of luminaries, power tool control with 2 no 9A contactors and raise lower push button, Incoming 35 sq. mm and out going 16 & 2.5 sq. mm terminals. | 1 | Nos. |  | 0
206 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
207 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 250 | M |  | 0
208 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 150 | M |  | 0
209 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 80 | M |  | 0
210 | EXTERNAL ELECTRICAL WORKS
211 | Supply and laying, Testing and commissioning of copper/GI Strips/wire for interconnecting the earthing stations ,panels, DBs etc. of the following sizes in built up trenches /surface/wall complete with holes & fixing, jointing / terminating accessories as per specifications & drawing complete as required. (Quantity shall be paid as per the actual measurement as executed, however direct measurement shall not exceed the quantity indicated in drawing approved)
212 | 25mmx 5 mm GI strip on surface or in recess | 250 | M |  | 0
213 | 6 SWG G.I wire on surface or in recess | 300 | M |  | 0
214 | Supply and creating of advance maintenance free Chemical Gel Earthing of Dual Pipe Technology (GI) of 3mtr long 50mm dia of outer shell (MS) with the 25mm dia of inner shell (MS) of 80-100 microns galvanized earth electrode filled with highly conducting metallic compounds with the permanent sealing’s at both the ends with the lead terminal of 32x10mm size at the top along with 50 Kgs of chemical mixture of Resistance Lowering Grounding Minerals. The loss on ignition by mass of the chemical compound shall be less than 20%. The chemical compound should be tested and certified by any International accredited and BIS (Bureau of Indian Standards) accredited laboratory. The earth electrode shall be duly tested & certified by CPRI (Central Power Research Institute), Govt of India. The chemical earth electrode manufacturer shall be an ISO 9001:2008 & ISO 14001:2004 certified organization. The Earth pit should be covered with heavy duty polyplastic weather proof chamber etc. as required & approved by the Engineer In charge. | 4 | Nos. |  | 0
215 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6 | Set |  | 0
216 | LT CABLES & EARTHING
217 | Supply of following size of 1.1 kv gradeFRLS aluminium conductor XLPE insulatedand PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
218 | 4 core, 25 Sq.mm. | 1500 | M |  | 0
219 | 4 core, 16 Sq.mm. | 500 | M |  | 0
220 | 4 core, 10 Sq.mm. | 200 | M |  | 0
221 | 4 core, 6 Sq.mm. | 200 | M |  | 0
222 | 3½ core X 70 Sq.mm. | 100 | M |  | 0
223 | 3½ core, 50 Sq.mm. | 100 | M |  | 0
224 | 3½ core, 185 Sq.mm. | 2200 | M |  | 0
225 | 3½ core, 300 Sq.mm. | 700 | M |  | 0
226 | Supply of following size of 1.1kv gradeFRLS multicore copper conductor XLPE insulatedand PVC sheathed armoured cable as per IS : 7098:1988 with upto date amendments.
227 | 4 core, 2.5 Sq.mm. | 300 | M |  | 0
228 | 4 core, 4 Sq.mm. | 200 | M |  | 0
229 | 4 core, 25 Sq.mm. | 100 | M |  | 0
231 | 3 core, 4 Sq.mm. | 500 | M |  | 0
232 | 1 core, 16 Sq.mm. | 100 | M |  | 0
233 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Tagging on both the ends will be done with aluminium tags etc. complete as required.
234 | Upto 35 sq. mm | 1000 | M |  | 0
235 | Above 35 sq. mm and upto 95 sq. mm | 50 | M |  | 0
236 | Above 95 sq. mm and upto 185 sq. mm | 150 | M |  | 0
237 | Above 185 sq. mm and upto 400 sq. mm | 50 | M |  | 0
238 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing masonry open duct as required. Tagging on both the ends will be done with aluminium tags etc. complete as required.
239 | Upto 35 sq. mm | 1400 | M |  | 0
240 | Above 35 sq. mm and upto 95 sq. mm | 60 | M |  | 0
241 | Above 95 sq. mm and upto 185 sq. mm | 1800 | M |  | 0
242 | Above 185 sq. mm and upto 400 sq. mm | 550 | M |  | 0
243 | Laying of one number PVC insulated and PVC sheathed / XLPEpower cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
244 | Upto 35 sq. mm | 1000 | M |  | 0
245 | Above 35 sq. mm and upto 95 sq. mm | 75 | M |  | 0
246 | Above 95 sq. mm and upto 185 sq. mm | 150 | M |  | 0
247 | Above 185 sq. mm and upto 400 sq. mm | 50 | M |  | 0
248 | Supplying and making indoor end termination with brass double compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
249 | 4 core, 35 Sq.mm. | 8 | Set |  | 0
250 | 4 core, 25 Sq.mm. | 72 | Set |  | 0
251 | 4 core, 16 Sq.mm. | 78 | Set |  | 0
252 | 4 core, 10 Sq.mm. | 6 | Set |  | 0
253 | 4 core, 6 Sq.mm. | 6 | Set |  | 0
254 | 3½ core X 300 Sq.mm. | 4 | Set |  | 0
255 | 3½ core X 185 Sq.mm. | 14 | Set |  | 0
256 | 3½ core X 95 Sq.mm. | 10 | Set |  | 0
257 | 3½ core X 70 Sq.mm. | 6 | Set |  | 0
258 | 3½ core, 50 Sq.mm. | 6 | Set |  | 0
259 | Supply and making indoor end terminationwith double brass compression gland and Copper lugs for XLPE insulated and PVC sheathed copper conductor cable of 1.1kv grade of the following sizes as required.
260 | 4 core, 6 Sq.mm. | 10 | Set |  | 0
261 | 4 core, 4 Sq.mm. | 14 | Set |  | 0
262 | 3 core, 4 Sq.mm. | 22 | Set |  | 0
263 | Cable Tray
264 | Supply and installation of following size of (Hot dip) GI Ladder type cable trays(Galvanisation thickness not less than 50 micron) in convenient sections, joined with connectors including horizontal and vertical bends, reducers, tees, cross members, clamps, connection pieces and other accessories as required, duly suspended from the ceiling with GI suspenders including GI bolts & GI nuts, etc. complete as required.
265 | 300mm 50mm 1.6mm thickness | 20 | M |  | 0
266 | Supply and installing of following size of (Hot dip) GI Perforated type cable trays (Galvanisation thickness not less than 50 micron) in convenient sections, joined with connectors including horizontal and vertical bends, reducers, tees, cross members, clamps, connection pieces and other accessories as required, duly suspended from the ceiling GI suspenders including GI bolts & GI nuts including fabrication, etc. complete as required.
267 | 150mm 50mm 1.6mm thickness | 200 | M |  | 0
268 | 300mm 50mm 1.6mm thickness | 120 | M |  | 0
269 | GI Raceway & Junction boxes
270 | Supply, assembly and laying of under floor trunking made out of 1.6mm thick GI sheet complete with jointing sleeve, horizontal bends, vertical bends, level adjustment components and closer, vertical elbow, covers, access outlet. etc. complete with all other accessories under floor installation including cutting and chasing the floor/ or on surface, making good the same, placing in position and cleaning from inside complete etc. as required.
271 | 300 mm x 38 mm (3 compartment) | 200 | M |  | 0
272 | 150 mm x 38 mm (2 compartment) | 150 | M |  | 0
273 | 100 mm x 38 mm (2 compartment) | 50 | M |  | 0
274 | 50 mm x 38 mm (1 compartment) | 100 | M |  | 0
275 | Providing and fixing 400 x 400 x 50 mm deepGI (hot dip galvanized) floor raceways junction box made out of 1.6 mm thick sheet steel as per specification. | 5 | Nos. |  | 0
276 | Providing and fixing 250 x 250 x 50 mm deepGI (hot dip galvanized) floor raceways junction box made out of 1.6 mm thick sheet steel junction box as per specification. | 30 | Nos. |  | 0
277 | Providing and fixing 150 x 150 x 50 mm deepGI (hot dip galvanized) floor raceways junction box made out of 1.6 mm thick sheet steel junction box as per specification. | 30 | Nos. |  | 0
278 | MISCELLANEOUS - SUB STATION ITEMS
279 | Supplying and fixing of nominal 2.0mm thick +/-10% thick, 3.3 KV working voltage level grade, 1000mm wide antistatic electric insulating mats conforming to IS:15652 with upto date amendments along with suitable adhesive/resin, sealing material and similar type of taping on sealing at all joints and corners as per recommendations prescribed by IS, complete as required & approved by Engineer Incharge. | 50 | Sqm. |  | 0
280 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enamelled white on both sides, and with inscription in single red colour on front side as required. | 10 | Nos. |  | 0
281 | Supplying & fixing of fire sealants to shafts, ceiling, cut-outs etc. with 2 hour fire rated composition as per specifications, NEC2011, relevant IS & as per approved makes of material & making good the same complete with accessories as required per site | 30 | Sqm |  | 0
282 | Supply of Rack type mobile charging station made of MS/ABS plastic enclosure duly powder coated having LED display of reputed make, operating on 230V, 50 Hz AC supply, capable of charging multiple devices (mobile phones/laptops, min 10 nos.) simultaneously through power socket & USB socket outlet, with built in protection device to prevent overcharging, USB & HDMI port for communication interface, drivers etc. as required, complete with required accessories for direct installation at site.(Equivalent to Z&D 101 Airport Mobile Charging station model) | 10 | Nos. |  | 0
283 | Dismatle of Escalator of at Existing Arrival Area (Old Terminal building) Dismantling of existing ThyssenKrupp make ESL-8 model Escalator with all accessories including minor civil work such as degrouting of structurers etc. with all out going power and control copper cables, terminations, interconnectionsetc. and The job also includes shifting of the dismantalled material from existing site and handing over to AAI store as per instruction of Engineer in-charge. | 1 | Job |  | 0
284 | Dismatle of Lift of at Existing Arrival Area (Old Terminal building) Dismantling of existing ThyssenKrupp make TCM-MC2 model Lift with all accessories including minor civil work such as degrouting of structurers etc. with all out going power and control copper cables, terminations, interconnectionsetc. and The job also includes shifting of the dismantalled material from existing site and handing over to AAI store as per instruction of Engineer in-charge. | 1 | Job |  | 0
285 | Dismantling of Electrical Items of Existing Arrival Area (Old Terminal building) Dismantling of existing Electrical system which includes all types led light fittings, DBs with all accessories, switches,sockets,regulators,Modular box,coverplates,jucntion boxes,wirings, 05 nos. electrical panels,signage boardsetc. with all accessories including minor civil work such as degrouting of structurers etc. with all out going power and control copper cables, terminations, interconnections, earthing etc. and The job also includes shifting of the dismantalled material from existing site and handing over to AAI store as per instruction of Engineer in-charge. | 1 | Lot |  | 0
286 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 2 | Each |  | 0
287 | Providing and fixing G.I. tape 20 mm X 3 mm thick on carapet or surfaceof wall for lightning conductor complete as required. (For horizontal run) | 250 | Mtr. |  | 0
288 | Providing and fixing G.I. tape 20 mm X 3 mm thick on carapet or surfaceof wall for lightning conductor complete as required. (For vertical run) | 150 | Mtr. |  | 0
289 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrodedirectly in ground as required. | 250 | Mtr. |  | 0
290 | Fountain type water cooler Work
291 | Supply, installation, testing & commissioning of recessed type bi level, mechanical cum sensor operated drinking water fountain with 2 nos stainless steel finish bubblers and integrated bottle filling station with dual dispenser of hot and cold water. Drinking water fountain shall be with filtration unit of UV, sediment and carbon filter of 150 LPH capacity with HPN pressurize system of tank capacity of 60 liter, cooling system of 60LPH capacity suitable to R-134(a) refrigerant with chilled water tank and 20 LPH heating capacity unit with tank of minimum 1.5 liter with adjustable thermostate included for both. Fountain shall be made of stainless steel (SS-304) body, bubbler shall be SS finish, including all accessories etc. complete as required and decided by E-I-C. The fountain shall be suitable for 230V +/- 10V,50 Hz AC supply. It shall comply with ANSI 117.1 and ADA and shall be GRIHA certified. | 2 | Each |  | 0
292 | Supply, Installation, Testing & Commissioning of Reverse Osmosis System (RO) having min. capacity 50 LPH RO system along with five stage filteration along with media and carbon filter , RO membrane , UV filteration & TDS meter and pressure gauge with 60 ltrs. HTP pressure tank to generate the adequate pressure for meeeting the operation for above item no. 75 . All the system will be enclosed in the powder coated M.S body with suitable mounting/fixing arrangment as per site requirement complete etc as required upto the satisfaction of Engg. In Charge. | 2 | Each |  | 0
293 | Hand Dryer
294 | Supply, installation, testing and commisioning of Recessed Automatic stainless steel Paper dispenser (3 in 1) along with Hi speed Hand Dryer and waste receptacle including all necessary accessories complete as required including minor civil works to complete the job. | 3 | Each |  | 0
295 | Supply, installation, testing and commisioning of Recessed stainless steel Tissue paper dispenser with waste receptacle (2 in 1) including all necessary accessories complete as required including minor civil works to complete the job. | 2 | Each |  | 0
296 | Supply, installation, testing and commisioning of Baby Diaper Changing Stationsmade of ABS Plastic including all necessary accessories complete as required including minor civil works to complete the job. | 2 | Each |  | 0
297 | Supply, installation, testing and commisioning of Baby Protection Seat including all necessary accessories complete as required including minor civil works to complete the job. | 2 | Each |  | 0
298 | SITC of STAINLESS STEEL Hand Dryer Made up of SS 304 Body Top. Fan Motor cum heater assembly for hot air blowing ,Temperature over heatprotection ,Sensor for auto operation ,Auto timer protection ,Low Noise suitable for 230v 50hz supply for Hand Drying Applications complete as required. | 4 | Each |  | 0
299 | Providing and fixing of frameless Automatic bi-parting sliding door operator for clear opening size of as mentioned above, modular design, including internal cover, eagle sensors on both sides, Electro mechanical lock, light barriers and programmer switch complete, With Operator Dimensions (L x H x T): 4170 x 123 x 150 mm approx. The track profile should be separate from the main profile for enabling reduction in vibration. Microprocessor control, self-learning, reversing when obstruction is encountered. Microprocessor- controlled control unit. It should be self-learning, with adjustable parameters for opening and closing speed,hold-open time and opening and closing force. Class of protection IP 20. The glasses shall be of 12mm clear toughened frameless with polished edge. The system should be suitable to operate on 230 V, AC, 50 Hz, 1-phase supply for following opening size all complete as per design and instructions of Engineer-In-Charge. (size of opening 3000 mm x 2400 mm height) | 2 | Each |  | 0
300 | Internal and external Signages
301 | Vehicular Directional Sign - Pole Mounted Drg. No. - Refer design drawing 1.3a-1G Providing and fixing Non-illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-In-Charge. All exterior signs should be manufactured considering harsh outdoor conditions, weatherproofing techniques and materials shall be used. Sign Face: Providing and fixing sign face panels 3 mm thick Aluminium sheet fabrication, Aluminium sheet fixed to sign frame. White retro-reflective vinyl pasted edge to edge over aluminium sheet. Graphics in plotter cut RAL 5013 exterior grade opaque vinyl pasted over white retro reflective vinyl. Sign Frame: Providing and fixing sign frame 50 x 50 x 2 mm in M.S. square section hot dipped galvanized and P.U. Paint to match RAL 9006 as per drawing. Frame to be directly fixed to the sign structure. Frame to receive the sign faces Sign Structure: MS square post 125x125x4 and horizontal square sections 75x75x2.5mm, hot dipped galvanized and powder coated to match RAL 9006. Post including welded MS base Plate and Gussets in 6mm thick MS Plate as per drawing with holes to fix it on holding down bolts anchored in concrete footing. The post shall closed with a 3 mm thick MS plate and parts kept unpainted to weld the sign structure as per the drawing to ensure a rigid connection at site. The entire post assembly shall be hot dipped galvanized and P.U. Painted to match RAL 9006 as specified and approved by the Engineer-In-Charge. The Post shall be always be a single continuous elemen without any joints. Cost to include all activities and temporary props used for a perfect vertical in plumb installation, shim Plates for adjustment of levels and filling the gap with concrete slurry etc. required for fixing the si in an external location. Secret fixing methods should be used to fix parts together. 225 x 225 mm size, 5 mm thick cover plate mounted in case the flooring is present. Foundation: Providing and laying foundation for the sign including its compaction and all activities like Excavation, PCC base layer, providing and fixing in position electrical connection wherever applicable and finished as per drawing. The item cost includes cutting and opening the floor finish at location, and making good the location to the match the original finish after fixing and installation of sign Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing. Size - 2100 X 1300 MM | 1 | Job |  | 0
302 | Traffic Statutory Sign Drg. No. - Refer design drawing 1.4aG Providing and fixing Non-illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge. All exterior signs should be manufactured considering harsh outdoor conditions, weatherproofing techniques and materials shall be used. Sign Face: Providing and fixing sign face panels 3 mm thick Aluminium sheet fixed to sign structure. White retro-reflective vinyl pasted over edge to edge aluminium sheet. Graphics in plotter cut red Pantone 485C and black Pantone 6C exterior grade opaque vinyl pasted over white retro reflective vinyl. Size : 600 X 600 MM | 4 | Job |  | 0
303 | Ceiling Hung Directional Sign Refer design drawing 2.1aS Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make Single side / Double side as approved by the Engineer-in- Charge. Sign Frame : Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Suspender : Providing and fixing Stainless steel 30 X 30 mm Hollow sections (assuming typical length of 1 meter) mounted on slabs/beams/walls. Lighting : All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing.
304 | 1 Message - Size 2100 X 255 MM | 2 | Job |  | 0
305 | 2 Message - Size - 2100 X 515 MM | 2 | Job |  | 0
306 | 3 Message - Size - 2100 X 775 MM | 2 | Job |  | 0
307 | Floor mounted directional sign - Refer design drawing 2.1b-1G Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign Face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make Single side / Double side as approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign Structure : All structural members in SS square post 100 x 100 X 3 mm and horizontal cross tie member square sections 50 X 50 X 2mm, brush finished. Base plate embedded below the floor finish and provided with a floor trim ring. hardware used for fixing of sign shall be Stainless steel. Post including SS base Plate and Gussets in 6mm thick SS Plate as per drawing with holes to fix it on holding down bolts anchored in concrete slab. The post shall clos with a 3 mm thick SS plate as specified and approved by the Engineer-In- Charge. Cost to include all activities and temporary props used for a perfect vertical in plumb installation, etc. required for fixing the sign in an internal location. Secret fixing methods should be used to fix parts together. Tension Rod: Providing and fixing tension rod in brush finished S.S. with the turn buckle system. Tension rod shall be fixed to the sign structure and the sign frame with S.S. gusset plates. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws, rivets, bolts, washers, nuts, etc. complete as per drawing. Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing.
308 | 2 Message - Size - 2100 X 515 MM | 2 | Job |  | 0
309 | 3 Message - Size - 2100 X 775 MM | 1 | Job |  | 0
310 | Counter Mounted Facility Announcer with Screen (43" FIDS by Client) (With S S Pole) Drg. No. Refer design drawing 2.2d-2G Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 70mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign Structure : All structural members in SS square post 100 x 100 x 3 mm, brush finished. base plate embedded below the floor finish and provided with a floor trim ring. All hardware used for fixing of sign shall be Stainless steel. Post including SS base Plate and Gussets in 6mm thick SS Plate as per drawing with holes to fix it on holding down bolts anchored in concrete slab. The post shall closed with a 3 mm thick SS plate as specified and approved by t Engineer-In-Charge. Cost to include all activities and temporary props used for a perfect vertical in plumb installation, etc. required for fixing the sign in an internal location. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Information Panel / FIDS Necessary provision should be made to accommodate 43"" LED / LCD TV as per site condition(LED TV will be arranged by AAI). Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing etc. as required as per site condition. Size : 1500 X 600 MM | 16 | Job |  | 0
311 | Lift Directory Drg. No. -Refer design drawing 2.3b-S Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign Face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Size : 800 X 460 | 2 | Job |  | 0
312 | Boarding Gates - Wall Mounted (43" FIDS by Client) Refer design drawing 2.2g-3-G Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 70mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Information Panel / FIDS Necessary provision should be made to accommodate 43" LED / LCD TV as per site condition (LED TV will be arranged by AAI). Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws, rivets, bolts, washers, nuts, etc. complete as per drawing etc. as required as per site condition. Size : 3000 X 600 MM | 3 | Job |  | 0
313 | Baggage Screening Pole Refer design drawing 2.2j-1-SProviding and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign Face : Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Sign Structure : All structural members in SS square post 100 x 100 X 3 mm brush finished. Base plate embedded below the floor finish and provided with a floor trim ring. All hardware used for fixing of sign shall be Stainless steel. Post including SS base Plate and Gussets in 6mm thick SS Plate as per drawing with holes to fix it on holding down bolts anchored in concrete slab. The post shall closed with a 3 mm thick SS plate as specified and approved by t Engineer-In- Charge. Cost to include all activities and temporary props used for a perfect vertical in plumb installation, etc. required for fixing the sign in an internal location. Secret fixing methods should be used to fix part together. Lighting : All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Accessories : Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing. Size : 900 X 450 MM | 2 | Job |  | 0
314 | Utility Signs 2.4a - Washroom / Drinking Water / Baby care Drg. No. -Refer design drawing 2.4a-S Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in Charge Sign Face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Size : 450 X 450 MM
315 | Wall Mounted - Size : 450 X 450 MM | 4 | Job |  | 0
316 | Wall Projected (Double Sided) - Size : 450 X 450 MM | 4 | Job |  | 0
317 | Lift Sign Lift No Sign Drg. No. -Refer design drawing 2.4c-S Providing and fixing illuminated signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge Sign Face Sign face shall be made in 5mm thick 040 white acrylic (as specified) having graphics pasted in Plotter cut Block out vinyl. The Plotter cut block out vinyl shall match the specified colour (colour Pantone Black 6C) and vinyl for text Pantone yellow C or Cyan 311C as per graphics and of specified make duly approved by the Engineer-in- Charge. Sign Frame: Providing and fixing sign frame 60mm wide Powder coated, colour RAL 9006 aluminium extrusion with inbuilt frame to receive the sign face. The sign face shall be fixed to sign frame with VHB tape in one side and Hook & Loop tape from the other side so as the panel be easily openable for maintenance. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. | 2 | Job |  | 0
318 | Emergency Direction Signs - Illuminated Drg. No. - Refer design drawing 2.6a-G Providing and fixing illuminated emergency signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer-in- Charge. Sign face: Sign face shall be made in 8 mm thick 040 having graphics pasted as per design. Sign Box: The sign box 80 mm deep shall be made out of 1.6 mm thick CRCA MS sheet fabricated and provided with same material support channel and ties welded to sign channel. All fabrication shall be done using CNC machines. Sign box shall be provided with openings with frosted glass at bottom and Mesh from inside on top for ventilation. Complete sign box including channel supports are to be powder coated to match RAL9016. Sign box flange receiving the sign face shall be provided with slots to receive the sign face. Lighting: All internal illumination shall be using LED strip edge Lights of approved make with electronic controllers, having even spread and overlaps to avoid banding and dark spots. Cost to include all internal connections and Wiring, terminating and connecting the incoming cable laid by Airport contractor at the site. Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws , rivets, bolts, washers, nuts, etc. complete as per drawing.
319 | Exit - Size - 675 X 255 MM | 20 | Job |  | 0
320 | Emergency Exit - Size - 900X 255 MM | 5 | Job |  | 0
321 | Assembly point Drg. No. - Refer design drawing 2.6c-G Providing and fixing Non-illuminated emergency signs including all operations from fabrication to installation all complete as per drawings, technical specifications, signage schedule and to the satisfaction of the Engineer- in- Charge. Sign face: Providing and fixing Photoluminescent signs made of inkjet printing using artworks provided and with photoluminescent material as per technical specifications. Inkjet printing shall be done on self-adhesive vinyl and pasted on 2mm thick powder coated white (RAL 9016) aluminium plate and fixed at location using screws. as per specification and using provided artwork including all operations from procuring the correct materials and made to sizes as specified and approved by the Engineer-in- charge. including all installation activities like marking, alignment and fixing with screws into the wall/cladding/face to the satisfaction of the Engineer-in- Charg Sign Frame: Internal MS structure receiving the signs faces using 25 X 25 X 3 equal angles and welded to the sign post. Sign Post: 100 mm OD MS post PU painted to match RAL 9011 grouted in ground with concrete footing as per detail. Accessories: Providing and fixing all accessories such as thimbles, end connectors, nut-inserts, screws, rivets, bolts, washers, nuts, etc. complete as per drawing. | 2 | Job |  | 0
322 | Emergency Signs - Fire life safety layout Drg. No. - Refer design drawing 2.6d-G Providing and fixing all Photoluminescent signs in the dedicated fire escape passages of the stations as per locations given in sign schedules, made of screen printed signs on white vinyl pasted over a 2mm thick aluminium sheet powder coated in White (RAL 9016) as per specification and using provided artwork including all operations from procuring the correct materials and made to sizes as specified and approved by the Engineer-In- Charge. including all installation activities like marking, alignment and fixing with screws into the wall/cladding/face to the satisfaction of the Engineer-In-Charge Size : 594 X 420 MM | 2 | Job |  | 0
323 | Fire Detection & Alarm system
324 | Supply, Installation , Testing & Commissioning of Network Repeater Panel with 240 x 64 LCD display; The LCD shall Display all events / detectors, devices status of complete systems in the networked, The NRP shall be equipped with QWERTY/ alphanumeric Keypad. Mounting options include an annunciator box, and blank modules are required for mounting.The repeater panel shall connect with existing Fire Alarm System network of the new terminal building. Make:Apollo-Advanced Model: MX-5020/FT | 1 | Nos. |  | 0
325 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable multicriteria detector (photoelectric smoke detection and thermal) with inbuilt isolator, multiple sensitivity modes,mounting base LED, Address/ Electronic Switch to programme the detectors. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-700APO + SA5000-200APO | 10 | Nos. |  | 0
326 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable smoke detector with inbuilt isolator, multiple sensitivity modes, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-600APO + SA5000-200APO | 220 | Nos. |  | 0
327 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable heat detector with fixed and rate of rise , with inbuilt isolator, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-400APO + SA5000-200APO | 4 | Nos. |  | 0
328 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable duct detector with auto floating sensitivity, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: 53456-022APO + 58000-600 | 10 | Nos. |  | 0
329 | Supplying, installation, testing & commissioning of Response Indicator which consists of steady glowing LED. This LED shall be mounted within a M.S. / Polycarbonate box and connected in parallel to the built in indicator of the detector as per specifications. The RI shall come "ON" as soon as the detector activates complete in all respects as per specification. Make:Apollo Model: 53832-070APO | 60 | Nos. |  | 0
330 | Supply, Installation, Testing and Commissioning of Addressable type Manual call Station complete with, all accessories as per specifications. (UL 9th Edition Approved/ EN54 and NFPA compliant or latest amended upto date) complete as required.The Manual call station shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5900-908APO | 20 | Nos. |  | 0
331 | Supply, Installation, Testing & Commissioning of supply with loop powered addressable sounder/hooter cum strobe suitable for 90db as per specifications. complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling as specified in NFPA 72 - 2007 edition. (UL Listed/ EN54 or latest amended upto date). The sounder strobe shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: 58000-005APO | 20 | Nos. |  | 0
332 | Supplying, Installing, Testing and Commissioning of addressable Control Module with relay etc. for Sounder, AHU, Fire Dampers, Smoke Ventilation complete as required and as per specifications. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date) complete as required.The module shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA4700-102APO | 50 | Nos. |  | 0
333 | Supplying, Installing, Testing and Commissioning of Intelligent Addressable motorised auto aligned Beam detector with transmitter & receiver with complete addressable modules capable of being addressed electronically. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date) complete as required.The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA7100-100APO + 29600-526 | 2 | Nos. |  | 0
334 | Providing and laying, connecting, testing & commissioning of 2 Core 1.5 Sq. mm, Glass Mica taped, with Cross Linked Halogen Free insulation, overall screened, HFLS, sheathed, fire resistant copper conductor twisted pair cable. The cable shall have CWZ rating to withstand temperature of 950°C complete with all accessories, terminations, glands etc. as per specification in all respect (FM Approved) as per BS 6387, BS 50200, basic design as per BS 7629. | 3500 | M |  | 0
335 | Programming, Graphic design for modified building, all fire alarm systemequipments programing etc as required to integrate with existing Fire Alarm Panel in NITB. | 1 | Job |  | 0
336 | Dismantling of Existing Fire Alarm System including one no. Edwards make EST-3 Fire panel (having 6 loop),fire survival cables, Approx. 250 smoke detectors, Approx. 20 MCPs, Approx. 10 Hooter-cum- strobe etc. and The job includes shifting of the dismantalled material from existing site and handing over to AAI store as per instruction of Engineer in-charge. | 1 | Job |  | 0
337 | Fire Fighting System
338 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required.
339 | 80 mm dia | 5 | Each |  | 0
340 | 100 mm dia | 5 | Each |  | 0
341 | 150 mm dia | 5 | Each |  | 0
342 | Providing, laying /erection, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling or with proper hanging arrangements (in case of sprinkler line with proper welding) with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required.
343 | 25 mm dia | 50 | Mtr |  | 0
344 | 32 mm dia | 50 | Mtr |  | 0
345 | 65 mm dia | 50 | Mtr |  | 0
346 | 80 mm dia | 50 | Mtr |  | 0
347 | 100 mm dia | 50 | Mtr |  | 0
348 | 150 mm dia | 500 | Mtr |  | 0
349 | Providing, laying /erection, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/ asphalt tape as per IS 10221, refilling the trench etc of following size
350 | 150 mm dia | 300 | Mtr |  | 0
351 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes i/c quartzoid bulb complete as required after removing existing MS sprinkler drop (if it is required) or making arrangements for fixing of sprinkler flexible pipe in case of new sprinkler line. a) 1500 mm | 120 | Each |  | 0
352 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 20 | Nos. |  | 0
353 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) female coupling suitable for connection with existing fire hydrant to the 63 mm dia hose pipe conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 20 | Nos. |  | 0
354 | Supplying and Fixing of M.S. Hose cabinet Wall mounted typefabricated out of S.S. sheet with glass fronted door and size of the cabinet shall be 600mm x 750 mm x 250 mm cabinet. | 10 | Nos. |  | 0
355 | Supplying and Fixing of First Aid Hose Reel, wall mounting swinging type complete with drum & bracket of MS construction, spray painted in Post office Red, confirming to IS 884/1995 with upto date amendments, complete with the following as required. 30 Meter long 20 mm dia water hose Thermoplastic (Textile reinforced) Type - 2 as per IS : 12585 25 mm dia ball valve & nozzle.Drum and rackets for fixing the equipments on wall.Connection from riser with stop valve (gun metal) & M.S. Pipe | 10 | Nos. |  | 0
356 | Providing and fixing pre fabricated 4 mm thick glass door (with SS frame) of size 2.1 m x 0.9 m with centre opening for fire hose cabinet suitably marked on the outside with letters “Fire Hose’’ including locking arrangement suitable to accommodate 1 no Hydrant landing valves, 1 no fire hose reel, 2 nos. 15m long 63 mm dia hose pipe , 1 no branch pipe, 1 no fire man’s axe and 2 nos fire extinguishers. All SS work to be in Red P.O Colour over appropriate primer. | 10 | Nos. |  | 0
357 | Dismantling and re-installation of existing fire fighting drop pipeas per site condition including accessories like socket, rozzar plate and cap etc as required and decded by E-I-C. | 26 | Each |  | 0
358 | SH- III AS & IT (PA system, FIDS, SCCTV & IT works)
359 | PA System
360 | Supply , Installation, Testing & Commissioning of IP based / Networked based Layer-2 or above protocol Digital Class-D multi channel Amplifier 600W total power output with 4 channel or more channel as specification / drawings and as directed by Engineer In Charge. | 2 | Nos |  | 0
361 | Supply , Installation, Testing & Commissioning of The desktop Paging station with extension keypad with 10 or more fully programmable keys for zone selection and PA system operation as per specification/drawings as directed by Engineer In Charge. | 2 | Nos |  | 0
362 | Supply , Installation, Testing & Commissioning of 6W ceiling mount EN 54 certified speaker with fire rated dome as per specification/drawings and as directed by Engineer In Charge. | 115 | Nos |  | 0
363 | Supply , Installation, Testing & Commissioning of Active Beam Steering loudspeaker, with 8x 4" driver, for minimum 20 mtrs throw as per specification/drawings as directed by Engineer In Charge. | 2 | Nos |  | 0
364 | Supply , Installation, Testing & Commissioning of 60W Line Array Outdoor Loudspeaker as per specification/drawings as directed by Engineer In Charge. | 3 | Nos |  | 0
365 | Supply of Noise sensing microphone, Omni-directional MEMS microphone for noise level tracking, as per specification/drawings as directed by Engineer In Charge. | 3 | Nos |  | 0
366 | Supply & fixing of Volume control units housed in suitable housing to meet the requirement and as per specifications. Volume control units 12W | 3 | Nos |  | 0
367 | Supply, laying / fixing of Armored Fire Servival speaker cable 1.5 sqmm 2 core including end termination etc as per site requirements as per specifications in existing conduit and approved make. | 2000 | Mtr |  | 0
368 | Supply, Installation, Testing and Commissioning of 19 "Equipment Rack, 32U Made of MS for housing of all above equipment , front lockable glass door, Fan tray fro colling, Caster wheel base , Main Panel with Spike Buster, Indivdual FUSE power supply unit, including all internal wiring/ interconnection etc. complete as required. | 1 | Nos |  | 0
369 | Integration and configration with Exsiting PA system | 1 | Lot |  | 0
370 | FLIGHT INFORMATION DISPLAY SYSTEM (FIDS)
371 | Supply, Installation, Testing & Commissioning of 55" LCD Displays (With in-built Intelligent Controller) with wall/ ceiling Mounting Arrangement | 10 | Nos |  | 0
372 | Supply, Installation, Testing & Commissioning of 42/43" LCD Displays (With in-built Intelligent Controller) with wall/ ceiling Mounting Arrangement | 25 | Nos |  | 0
373 | Integration with AODB and other systems as required | 1 | Lum |  | 0
374 | Charges for the installation, Integration, Testing and Commissioning of the complete System with necessary softwares and power distribution boards, power point boxes etc. as per required with 3 years contract period | 1 | Lot |  | 0
375 | Supply of Layer 2 network Switch 24 ports as per technical specifications with 19" wall mount Network Rack of suitable size, Jack Panel & other accessories | 3 | Nos |  | 0
376 | Supply of 12 Ports Light Interface Unit (LIU) fully populated with modules/ adapters as per site requirement | 1 | Nos |  | 0
377 | Supply & Laying 6 core MMF OFC armored cable on wall/ surface/ tray with accessories as required | 800 | mtrs |  | 0
378 | Supply & Laying of UTP Cat 6 cable in existing conduit tray with accessories including termination with v,/all/ surface mount box as required. | 1500 | mtrs |  | 0
379 | Supply & Laying of 3 Core 1 .5 sq mm multistrand copper conductor PVC insulated PVC sheathed unarmored power cable in existing conduit tray with accessories as required | 1000 | mtrs |  | 0
380 | Supply & Laying of 3 Core 6 sq mm multistrand copper conductor PVC insulated PVC sheathed armored power cable on wall/ surface/ tray with accessories as required | 1000 | mtrs |  | 0
381 | Supply & Laying of 25 mm dia, 16 SWG ISI marked PVC conduit with accessories as required | 1000 | mtrs |  | 0
382 | Supply of RJ45 I/O face plate gang box with standard length of patch cable for FID System as per site requirement and Specifications. | 50 | Nos |  | 0
383 | CCTV
384 | Supply of Outdoor Color Dome PTZ Cameracomplete with camera mount and all accessories as per specifications. | 3 | Nos. |  | 0
385 | Supply of Indoor Color Dome PTZ Cameracomplete with camera mount and all accessories, as per specifications. | 3 | Nos. |  | 0
386 | Supply of Varifocal Outdoor Fixed Color Box Cameracomplete with camera mount and all accessories, as per specifications. | 10 | Nos. |  | 0
387 | Supply of Varifocal Fixed Outdoor Color Dome Cameracomplete with camera mount and all accessories, as per specifications. | 10 | Nos. |  | 0
388 | Supply of Varifocal Indoor Fixed Colour Dome Cameracomplete with camera mount and all accessories, as per specifications. | 40 | Nos. |  | 0
389 | Supply of PTZ Camera Joystick complete with all accessories, as per specifications. | 2 | Nos. |  | 0
390 | Supply of 24 Port Core Layer-3 Switch with fully polulated 16 Nos. of 1 Gbps Copper Ports and 8 Nos. of Fiber Ports fully polulated with 10G SFP+ module,Jack Panel and other accessories. | 2 | Nos. |  | 0
391 | Supply of Layer-2 Switch (24 Nos. of 10/100/1000 Mbps PoE+ Copper (Ethernet) Ports (30W per port) and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 6 | Nos. |  | 0
392 | Supply of RJ-45 IO Faceplate with Gang box/Back box with standard length of patch cable, as per site requirement with technical specifications as per bid document. | 70 | Nos. |  | 0
393 | Supply of SFP+ Transceiver with all accessories as per specifications fully compatible with switch. | 16 | Nos. |  | 0
394 | Supply of MEDIA CONVERTERS complete with all accessories as per specifications. | 2 | Nos. |  | 0
395 | Supply of Network Attached Storage (NAS) per TB usable capacityon SAS/SATA Disk (in RAID 6 configuration) complete with all accessories, etc. as per specifications. | 200 | TB usable space |  | 0
396 | Supply of 55" Displays complete with wall/ceiling/floor mounting arrangement as per specifications. | 6 | Nos. |  | 0
397 | Supply of Client Workstation including licensed Operating System and Antivirus with Monitor, Joystick Keyboard or USB supported standard keyboard,supported with dual monitor, for one no.of 55" LED display and one No. of 21" display, Optical Scroll Mouse and all accessories, etc., as per specifications. | 5 | Nos. |  | 0
398 | Supply of Rack Mountable VMS +VA Main Server including licensed Operating system and Anti- virus complete with all accessories as per specifications. | 2 | Nos. |  | 0
399 | Supply of Rack Mountable VMS +VA Failover Server including licensed Operating system and Anti- virus, complete with all accessories as per specifications. | 1 | Nos. |  | 0
400 | Supply of 08 port KVM Switch with integrated 17" LCD/ LED Monitor, for connectivity with Servers in rack as per specifications. | 1 | Nos. |  | 0
401 | Supply of Surveillance CCTV 19" Equipment Rack (42 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 1 | Nos. |  | 0
402 | Supply of Surveillance CCTV 19" Equipment Rack (9 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 6 | Nos. |  | 0
403 | Supply of lifetime licensed VMS and Video Analytics Softwarefor complete system consisting of all Main Servers/all Client Workstations/ NAS, to be supplied with media (2 Nos. of Software CD) to meet the technical & functional requirements as per specifications. | 2 | Set |  | 0
404 | Supply of lifetime licensed VMS and Video Analytics Softwarefor complete system consisting of Failover Servers/all Client Workstations/ NAS, to be supplied with media (2 Nos. of Software CD) to meet the technical & functional requirements as per specifications. | 1 | Set |  | 0
405 | VMS Camera lifeitime Licence integrated in each Main Server VMS+VA Software. | 120 | Nos |  | 0
406 | VMS Camera lifeitime Licence integrated in Failover Server VMS+VA Software. | 120 | Nos |  | 0
407 | Video Analytics Camera lifetime License integrated in each Main ServerVMS+VA Software. | 40 | Nos. |  | 0
408 | Video Analytics Camera lifetime License integrated in Failover Server VMS+VA Software. | 40 | Nos. |  | 0
409 | Supply and laying of Optic Fibre Communication Outdoor cable (6 core, SMF, 9/125 µm, 10 Gbps)in existing pipe on surface/recess/concealed, with connectors/adaptors, termination etc. required as per specifications. | 2000 | Meters |  | 0
410 | Supply and laying of CAT-6 UTP Data Cable in existing conduit/pipe on surface/recess/concealed, with connectors, termination etc. required as per specifications. | 5000 | Meters |  | 0
411 | Supply and laying of 3 core 6 sqmm multi- strand copper conductor PVC insulated PVC sheathed armouredpower cable on surface/recess/ concealed including termination (at both ends), MCB, distribution box, all accessories etc. required as per specifications. | 3000 | Meters |  | 0
412 | Supply of 12 port Light guide Interconnect Unit (LIU)fully populated with modules/ adapters as per siterequirement and specifications. | 7 | Nos. |  | 0
413 | Supply and laying of MS Conduit with bends and tees complete with all accessories as per specifications. | 1000 | Meters |  | 0
414 | Supply and laying of PVC Conduit with bends and tees complete with all accessories as per specifications. | 2500 | Meters |  | 0
415 | Supply of CAT 6 PATCH PANEL complete with all accessories as per specifications. | 6 | Nos. |  | 0
416 | Supply of 10 KVA Online UPS with Battery Bank, Power Distribution Panels and complete required accessories as per specifications. | 2 | Nos. |  | 0
417 | Supply of Network Time Protocol (NTP) Server with accessories as per specifications. | 1 | No |  | 0
418 | Installation,Integration,Testing, Commissioning of the complete SCCTV Systemwith required accessories of all SCCTV equipment properly labelled including networking, cabling etc., configuration of individual equipment as per specifications, training & documentation along with hard copy with drawing/map layout of the entire system including softcopy in Autocad. | 1 | Job |  | 0
419 | Supply,Installation of the ANPR Cameras, its Integration with the existing INFINOVA MAKE ANPR Software. | 4 | Nos. |  | 0
420 | HHMD and LED TV
421 | Supply of 20 HHMD with 5 years warranty. Techno Logy / Dimensiobn Pulse Technology, 350 mm ( Minimum) Length Total (overall) (mm), Less than 350 gm Weight DETECION RANGE / SCAN RATE Ferrous Non Ferrous & Alloy Detection, 25 mm Detects Pin from a minimum distance of (mm) 150 mm Detects Pistol - 0.22 from a minimum distance of (mm): 50 mm Detects Cartridge - 0.22 from a minimum distance of (mm):, 25 mm Detects Razor Blade from a minimum distance of (mm):, Automatic Tuning to ensure equal results on wide range of metals and alloys, 400 mm/s Scan Rate (mm per Second) (mm/s) | 20 | Nos |  | 0
422 | Supply of LED Display with mounting arrangement LED Backlit Technology, 138 cm screen size ( Diagonal) Miimum (cm), Non Touch Screen type, In plane switching (IPS) Panel Technology, Portrait and landscape Orientation, 190 x 1080 ( Full HD) Native Resolution ( Pixels), 16:9 Aspect ratio, 450 nits Brightness ( Nits) minimum, 1100:1 bid MAF must Native Contrast Ratio minimum, 178:178 Viewing Angle (Horizontal: vertical), 12 ms Response Time (milli seconds), 11.9 mm Bezel width (mm), 2 Number of Speakers, Inbuilt Arrangement of Speakers, 20 Wattage of Speakers (with maximum 10% THD)(wATT), Avaiable of Output port for audio output if internal speakers are not there, avaiable VGA port HDMI port DVI _ D Port, Display Port, USB Port, RS 232 C port, RJ 45, In built sinage software, 100 w Power Consumption in Operating Mode (Maximum)(Watt), 0.5 Power Consumption in Sleep Mode (Maximum)(Watt), 24 x 7 Duty cycle, Wall mount Mounting aggangement, BIS registration under CRS of meity yes, IF yes BIS registration number R-75000191, ROHS complaiance yes, Power supply 230 V AC 50 Hz, 0 c- 40 C Operation temperature range ( Degree C), Operating Humdity( % RH) 10 %- 80 %, Dimension ( L x Bx H) 1238 x 714 x 54 cm, 50.1 Kg weight, Accessories to be supplied: AC Power cord remote control, user manual, wall mount bracket, necessary cables and connectors yes with on site OEM warrent 05 years | 10 | Nos |  | 0
423 | IT works
424 | Supply of Layer-2 Switch (Minimum 8 Nos. of 10/100/1000 Mbps PoE+ Copper (Ethernet) Ports (30W per port) and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 2 | Nos. |  | 0
425 | Supply of Layer-2 Switch (24 Nos. of 10/100/1000 Mbps Non PoE Copper (Ethernet) Ports and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 2 | Nos. |  | 0
426 | Supply of WiFi Access Points (HP Aruba AP 515) | 8 | Nos. |  | 0
427 | Supply of Field Termination Plug Shielded FTP at AP End | 10 | Nos. |  | 0
428 | Supply of RJ-45 IO Faceplate with Gang box/Back box with standard length of patch cable, as per site requirement with technical specifications as per bid document. | 40 | Nos. |  | 0
429 | Supply of SFP Transceiver 10G with all accessories as per specifications. | 10 | Nos. |  | 0
430 | Supply of IT Network Rack 19" Equipment Rack (9 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 3 | Nos. |  | 0
431 | Supply of IT Network rack 19" Equipment Rack (18 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 1 | Nos. |  | 0
432 | Supply, laying and splicing of Optic Fibre Communication Outdoor cable (12 core, SMF, 9/125 µm, 10 Gbps) in existing pipe on surface/recess/concealed, with connectors/adaptors, termination etc. required as per specifications. | 2000 | Mtr. |  | 0
433 | Supply and laying of CAT-6A UTP Data Cable in existing conduit/pipe on surface/recess/concealed, with connectors, termination etc. required as per specifications. | 5000 | Mtr. |  | 0
434 | Supply of 12 port Light guide Interconnect Unit (LIU) fully populated with modules/ adapters as per siterequirement and specifications. | 5 | Mtr. |  | 0
435 | Supply of PVC Conduit with bends and tees complete with all accessories as per specifications. | 500 | Mtr. |  | 0
436 | Supply of CAT 6A PATCH PANEL complete with all accessories as per specifications. | 6 | Nos. |  | 0
437 | Supply of 1 KVA UPS as per specifications. | 4 | Nos. |  | 0
438 | Work-Installation,Integration,Testing, Commissioning,Training of the complete system with required accessories of all equipment including networking, cable laying OFC and CAT 6, I/O Boxes etc. configuration of individual equipment as per specifications and integration with the existing system. | 1 | Job |  | 0
439 | SH-IV CAMC for Airport System
440 | COMPREHENSIVE AMC AFTER EXPIRY OF 1 YEAR Defective Liability Period for SCCTV
441 | One (01) resident Skilled Manpower [Minimum Graduate] having good knowledge/experience of Networking/ IT/SCCTV System is to be deployed during General shift (i.e., 0930 AM to 1800 PM) for Twenty-Six (26) days per month to carry out routine periodic preventivemaintenance of SCCTV system as per manufacturer recommendations or/as per direction of Officer In-charge during One (01) years contract period. | 12 | Month |  | 0
442 | First Year CAMC of all the items (from S.No 384 to 419) with provision of one skilled manpower (26 days/ month during general duty hours) of SCCTV System after DLP | 1 | Year |  | 0
443 | Second Year CAMC all the items (from S.No 384 to 419) with provision of one skilled manpower (26 days/ month during general duty hours) of SCCTV System after DLP | 1 | Year |  | 0
444 | COMPREHENSIVE AMC AFTER EXPIRY OF 1 YEAR Defective Liability Period for PA system
445 | Skilled Manpower for day to day routine maintenance of PA system for year DLP and 2 Year CAMC | 3 | Year |  | 0
446 | First Year Comprehensive AMC all the items (from S.No 360 to 369) installed with spares (after expiry of one year DLP) | 1 | Year |  | 0
447 | Second Year Comprehensive AMC all the items (from S.No 360 to 369) installed with spares (after expiry of one year DLP) | 1 | Year |  | 0
448 | COMPREHENSIVE AMC AFTER EXPIRY OF 1 YEAR Defective Liability Period for FIDS
449 | Skilled Manpower (One) for day to day routine maintenance of FIDS system for one year DLP and 2 Year CAMC | 3 | Year |  | 0
450 | First Year Comprehensive AMC all the items (from S.No 371 to 382) installed with spares (after expiry of one year DLP) | 1 | Year |  | 0
451 | Second Year Comprehensive AMC all the items (from S.No 371 to 382) installed with spares (after expiry of one year DLP) | 1 | Year |  | 0
Total in Figures |  |  |  |  | 0