## IT & OTHER WORKS BOQ
Name of Work: Reconstruction of Old Terminal Building at Pune Airport. Sub Head: Revamping of part old Terminal Building and Miscellaneous works for enhancing total passenger handling capacity at Pune Airport.
IT AND OTHER WORKS BOQ
Sl. No. | Item Description | Quantity | Units | Supply Rate | Installation Rate | Total Rate | Supply Amount | Installation Amount | Total Amount
1 | 2 | 3 | 4
323 | Fire Detection & Alarm system |  |  |  |  | 0 | 0 | 0 | 0
324 | Supply, Installation , Testing & Commissioning of Network Repeater Panel with 240 x 64 LCD display; The LCD shall Display all events / detectors, devices status of complete systems in the networked, The NRP shall be equipped with QWERTY/ alphanumeric Keypad. Mounting options include an annunciator box, and blank modules are required for mounting.The repeater panel shall connect with existing Fire Alarm System network of the new terminal building. Make:Apollo-Advanced Model: MX-5020/FT | 1 | Nos. |  |  | 0 | 0 | 0 | 0
325 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable multicriteria detector (photoelectric smoke detection and thermal) with inbuilt isolator, multiple sensitivity modes,mounting base LED, Address/ Electronic Switch to programme the detectors. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-700APO + SA5000-200APO | 10 | Nos. |  |  | 0 | 0 | 0 | 0
326 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable smoke detector with inbuilt isolator, multiple sensitivity modes, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-600APO + SA5000-200APO | 220 | Nos. |  |  | 0 | 0 | 0 | 0
327 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable heat detector with fixed and rate of rise , with inbuilt isolator, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. Detector shall withstand temp. variation from 0 to 50 degree C. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5100-400APO + SA5000-200APO | 4 | Nos. |  |  | 0 | 0 | 0 | 0
328 | Supply, Installation, Testing & Commissioning of Automatic Analogue addressable duct detector with auto floating sensitivity, mounting base LED, Address/ Electronic Switch to programme the detectors complete as required. Detector with inbuilt isolator can also be considered. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date). The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: 53456-022APO + 58000-600 | 10 | Nos. |  |  | 0 | 0 | 0 | 0
329 | Supplying, installation, testing & commissioning of Response Indicator which consists of steady glowing LED. This LED shall be mounted within a M.S. / Polycarbonate box and connected in parallel to the built in indicator of the detector as per specifications. The RI shall come "ON" as soon as the detector activates complete in all respects as per specification. Make:Apollo Model: 53832-070APO | 60 | Nos. |  |  | 0 | 0 | 0 | 0
330 | Supply, Installation, Testing and Commissioning of Addressable type Manual call Station complete with, all accessories as per specifications. (UL 9th Edition Approved/ EN54 and NFPA compliant or latest amended upto date) complete as required.The Manual call station shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA5900-908APO | 20 | Nos. |  |  | 0 | 0 | 0 | 0
331 | Supply, Installation, Testing & Commissioning of supply with loop powered addressable sounder/hooter cum strobe suitable for 90db as per specifications. complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling as specified in NFPA 72 - 2007 edition. (UL Listed/ EN54 or latest amended upto date). The sounder strobe shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: 58000-005APO | 20 | Nos. |  |  | 0 | 0 | 0 | 0
332 | Supplying, Installing, Testing and Commissioning of addressable Control Module with relay etc. for Sounder, AHU, Fire Dampers, Smoke Ventilation complete as required and as per specifications. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date) complete as required.The module shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA4700-102APO | 50 | Nos. |  |  | 0 | 0 | 0 | 0
333 | Supplying, Installing, Testing and Commissioning of Intelligent Addressable motorised auto aligned Beam detector with transmitter & receiver with complete addressable modules capable of being addressed electronically. (UL 9th Edition Approved and NFPA compliant/ EN54 or latest amended upto date) complete as required.The detector shall be compatible to the existing new terminal building fire alarm panel. Make:Apollo Model: SA7100-100APO + 29600-526 | 2 | Nos. |  |  | 0 | 0 | 0 | 0
334 | Providing and laying, connecting, testing & commissioning of 2 Core 1.5 Sq. mm, Glass Mica taped, with Cross Linked Halogen Free insulation, overall screened, HFLS, sheathed, fire resistant copper conductor twisted pair cable. The cable shall have CWZ rating to withstand temperature of 950°C complete with all accessories, terminations, glands etc. as per specification in all respect (FM Approved) as per BS 6387, BS 50200, basic design as per BS 7629. | 3500 | M |  |  | 0 | 0 | 0 | 0
335 | Programming, Graphic design for modified building, all fire alarm systemequipments programing etc as required to integrate with existing Fire Alarm Panel in NITB. | 1 | Job |  |  | 0 | 0 | 0 | 0
336 | Dismantling of Existing Fire Alarm System including one no. Edwards make EST-3 Fire panel (having 6 loop),fire survival cables, Approx. 250 smoke detectors, Approx. 20 MCPs, Approx. 10 Hooter-cum- strobe etc. and The job includes shifting of the dismantalled material from existing site and handing over to AAI store as per instruction of Engineer in-charge. | 1 | Job |  |  | 0 | 0 | 0 | 0
337 | Fire Fighting System |  |  |  |  | 0 | 0 | 0 | 0
338 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required. |  |  |  |  | 0 | 0 | 0 | 0
339 | 80 mm dia | 5 | Each |  |  | 0 | 0 | 0 | 0
340 | 100 mm dia | 5 | Each |  |  | 0 | 0 | 0 | 0
341 | 150 mm dia | 5 | Each |  |  | 0 | 0 | 0 | 0
342 | Providing, laying /erection, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling or with proper hanging arrangements (in case of sprinkler line with proper welding) with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. |  |  |  |  | 0 | 0 | 0 | 0
343 | 25 mm dia | 50 | Mtr |  |  | 0 | 0 | 0 | 0
344 | 32 mm dia | 50 | Mtr |  |  | 0 | 0 | 0 | 0
345 | 65 mm dia | 50 | Mtr |  |  | 0 | 0 | 0 | 0
346 | 80 mm dia | 50 | Mtr |  |  | 0 | 0 | 0 | 0
347 | 100 mm dia | 50 | Mtr |  |  | 0 | 0 | 0 | 0
348 | 150 mm dia | 500 | Mtr |  |  | 0 | 0 | 0 | 0
349 | Providing, laying /erection, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/ asphalt tape as per IS 10221, refilling the trench etc of following size |  |  |  |  | 0 | 0 | 0 | 0
350 | 150 mm dia | 300 | Mtr |  |  | 0 | 0 | 0 | 0
351 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes i/c quartzoid bulb complete as required after removing existing MS sprinkler drop (if it is required) or making arrangements for fixing of sprinkler flexible pipe in case of new sprinkler line. a) 1500 mm | 120 | Each |  |  | 0 | 0 | 0 | 0
352 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 20 | Nos. |  |  | 0 | 0 | 0 | 0
353 | Supply & fixing of 63 mm dia Stainless Steel (Grade 304) female coupling suitable for connection with existing fire hydrant to the 63 mm dia hose pipe conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling etc. as required. | 20 | Nos. |  |  | 0 | 0 | 0 | 0
354 | Supplying and Fixing of M.S. Hose cabinet Wall mounted typefabricated out of S.S. sheet with glass fronted door and size of the cabinet shall be 600mm x 750 mm x 250 mm cabinet. | 10 | Nos. |  |  | 0 | 0 | 0 | 0
355 | Supplying and Fixing of First Aid Hose Reel, wall mounting swinging type complete with drum & bracket of MS construction, spray painted in Post office Red, confirming to IS 884/1995 with upto date amendments, complete with the following as required. 30 Meter long 20 mm dia water hose Thermoplastic (Textile reinforced) Type - 2 as per IS : 12585 25 mm dia ball valve & nozzle.Drum and rackets for fixing the equipments on wall.Connection from riser with stop valve (gun metal) & M.S. Pipe | 10 | Nos. |  |  | 0 | 0 | 0 | 0
356 | Providing and fixing pre fabricated 4 mm thick glass door (with SS frame) of size 2.1 m x 0.9 m with centre opening for fire hose cabinet suitably marked on the outside with letters “Fire Hose’’ including locking arrangement suitable to accommodate 1 no Hydrant landing valves, 1 no fire hose reel, 2 nos. 15m long 63 mm dia hose pipe , 1 no branch pipe, 1 no fire man’s axe and 2 nos fire extinguishers. All SS work to be in Red P.O Colour over appropriate primer. | 10 | Nos. |  |  | 0 | 0 | 0 | 0
357 | Dismantling and re-installation of existing fire fighting drop pipeas per site condition including accessories like socket, rozzar plate and cap etc as required and decded by E-I-C. | 26 | Each |  |  | 0 | 0 | 0 | 0
358 | SH- III AS & IT (PA system, FIDS, SCCTV & IT works) |  |  |  |  | 0 | 0 | 0 | 0
359 | PA System |  |  |  |  | 0 | 0 | 0 | 0
360 | Supply , Installation, Testing & Commissioning of IP based / Networked based Layer-2 or above protocol Digital Class-D multi channel Amplifier 600W total power output with 4 channel or more channel as specification / drawings and as directed by Engineer In Charge. | 2 | Nos |  |  | 0 | 0 | 0 | 0
361 | Supply , Installation, Testing & Commissioning of The desktop Paging station with extension keypad with 10 or more fully programmable keys for zone selection and PA system operation as per specification/drawings as directed by Engineer In Charge. | 2 | Nos |  |  | 0 | 0 | 0 | 0
362 | Supply , Installation, Testing & Commissioning of 6W ceiling mount EN 54 certified speaker with fire rated dome as per specification/drawings and as directed by Engineer In Charge. | 115 | Nos |  |  | 0 | 0 | 0 | 0
363 | Supply , Installation, Testing & Commissioning of Active Beam Steering loudspeaker, with 8x 4" driver, for minimum 20 mtrs throw as per specification/drawings as directed by Engineer In Charge. | 2 | Nos |  |  | 0 | 0 | 0 | 0
364 | Supply , Installation, Testing & Commissioning of 60W Line Array Outdoor Loudspeaker as per specification/drawings as directed by Engineer In Charge. | 3 | Nos |  |  | 0 | 0 | 0 | 0
365 | Supply of Noise sensing microphone, Omni-directional MEMS microphone for noise level tracking, as per specification/drawings as directed by Engineer In Charge. | 3 | Nos |  |  | 0 | 0 | 0 | 0
366 | Supply & fixing of Volume control units housed in suitable housing to meet the requirement and as per specifications. Volume control units 12W | 3 | Nos |  |  | 0 | 0 | 0 | 0
367 | Supply, laying / fixing of Armored Fire Servival speaker cable 1.5 sqmm 2 core including end termination etc as per site requirements as per specifications in existing conduit and approved make. | 2000 | Mtr |  |  | 0 | 0 | 0 | 0
368 | Supply, Installation, Testing and Commissioning of 19 "Equipment Rack, 32U Made of MS for housing of all above equipment , front lockable glass door, Fan tray fro colling, Caster wheel base , Main Panel with Spike Buster, Indivdual FUSE power supply unit, including all internal wiring/ interconnection etc. complete as required. | 1 | Nos |  |  | 0 | 0 | 0 | 0
369 | Integration and configration with Exsiting PA system | 1 | Lot |  |  | 0 | 0 | 0 | 0
370 | FLIGHT INFORMATION DISPLAY SYSTEM (FIDS) |  |  |  |  | 0 | 0 | 0 | 0
371 | Supply, Installation, Testing & Commissioning of 55" LCD Displays (With in-built Intelligent Controller) with wall/ ceiling Mounting Arrangement | 10 | Nos |  |  | 0 | 0 | 0 | 0
372 | Supply, Installation, Testing & Commissioning of 42/43" LCD Displays (With in-built Intelligent Controller) with wall/ ceiling Mounting Arrangement | 25 | Nos |  |  | 0 | 0 | 0 | 0
373 | Integration with AODB and other systems as required | 1 | Lum |  |  | 0 | 0 | 0 | 0
374 | Charges for the installation, Integration, Testing and Commissioning of the complete System with necessary softwares and power distribution boards, power point boxes etc. as per required with 3 years contract period | 1 | Lot |  |  | 0 | 0 | 0 | 0
375 | Supply of Layer 2 network Switch 24 ports as per technical specifications with 19" wall mount Network Rack of suitable size, Jack Panel & other accessories | 3 | Nos |  |  | 0 | 0 | 0 | 0
376 | Supply of 12 Ports Light Interface Unit (LIU) fully populated with modules/ adapters as per site requirement | 1 | Nos |  |  | 0 | 0 | 0 | 0
377 | Supply & Laying 6 core MMF OFC armored cable on wall/ surface/ tray with accessories as required | 800 | mtrs |  |  | 0 | 0 | 0 | 0
378 | Supply & Laying of UTP Cat 6 cable in existing conduit tray with accessories including termination with v,/all/ surface mount box as required. | 1500 | mtrs |  |  | 0 | 0 | 0 | 0
379 | Supply & Laying of 3 Core 1 .5 sq mm multistrand copper conductor PVC insulated PVC sheathed unarmored power cable in existing conduit tray with accessories as required | 1000 | mtrs |  |  | 0 | 0 | 0 | 0
380 | Supply & Laying of 3 Core 6 sq mm multistrand copper conductor PVC insulated PVC sheathed armored power cable on wall/ surface/ tray with accessories as required | 1000 | mtrs |  |  | 0 | 0 | 0 | 0
381 | Supply & Laying of 25 mm dia, 16 SWG ISI marked PVC conduit with accessories as required | 1000 | mtrs |  |  | 0 | 0 | 0 | 0
382 | Supply of RJ45 I/O face plate gang box with standard length of patch cable for FID System as per site requirement and Specifications. | 50 | Nos |  |  | 0 | 0 | 0 | 0
383 | CCTV |  |  |  |  | 0 | 0 | 0 | 0
384 | Supply of Outdoor Color Dome PTZ Cameracomplete with camera mount and all accessories as per specifications. | 3 | Nos. |  |  | 0 | 0 | 0 | 0
385 | Supply of Indoor Color Dome PTZ Cameracomplete with camera mount and all accessories, as per specifications. | 3 | Nos. |  |  | 0 | 0 | 0 | 0
386 | Supply of Varifocal Outdoor Fixed Color Box Cameracomplete with camera mount and all accessories, as per specifications. | 10 | Nos. |  |  | 0 | 0 | 0 | 0
387 | Supply of Varifocal Fixed Outdoor Color Dome Cameracomplete with camera mount and all accessories, as per specifications. | 10 | Nos. |  |  | 0 | 0 | 0 | 0
388 | Supply of Varifocal Indoor Fixed Colour Dome Cameracomplete with camera mount and all accessories, as per specifications. | 40 | Nos. |  |  | 0 | 0 | 0 | 0
389 | Supply of PTZ Camera Joystick complete with all accessories, as per specifications. | 2 | Nos. |  |  | 0 | 0 | 0 | 0
390 | Supply of 24 Port Core Layer-3 Switch with fully polulated 16 Nos. of 1 Gbps Copper Ports and 8 Nos. of Fiber Ports fully polulated with 10G SFP+ module,Jack Panel and other accessories. | 2 | Nos. |  |  | 0 | 0 | 0 | 0
391 | Supply of Layer-2 Switch (24 Nos. of 10/100/1000 Mbps PoE+ Copper (Ethernet) Ports (30W per port) and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 6 | Nos. |  |  | 0 | 0 | 0 | 0
392 | Supply of RJ-45 IO Faceplate with Gang box/Back box with standard length of patch cable, as per site requirement with technical specifications as per bid document. | 70 | Nos. |  |  | 0 | 0 | 0 | 0
393 | Supply of SFP+ Transceiver with all accessories as per specifications fully compatible with switch. | 16 | Nos. |  |  | 0 | 0 | 0 | 0
394 | Supply of MEDIA CONVERTERS complete with all accessories as per specifications. | 2 | Nos. |  |  | 0 | 0 | 0 | 0
395 | Supply of Network Attached Storage (NAS) per TB usable capacityon SAS/SATA Disk (in RAID 6 configuration) complete with all accessories, etc. as per specifications. | 200 | TB usable space |  |  | 0 | 0 | 0 | 0
396 | Supply of 55" Displays complete with wall/ceiling/floor mounting arrangement as per specifications. | 6 | Nos. |  |  | 0 | 0 | 0 | 0
397 | Supply of Client Workstation including licensed Operating System and Antivirus with Monitor, Joystick Keyboard or USB supported standard keyboard,supported with dual monitor, for one no.of 55" LED display and one No. of 21" display, Optical Scroll Mouse and all accessories, etc., as per specifications. | 5 | Nos. |  |  | 0 | 0 | 0 | 0
398 | Supply of Rack Mountable VMS +VA Main Server including licensed Operating system and Anti- virus complete with all accessories as per specifications. | 2 | Nos. |  |  | 0 | 0 | 0 | 0
399 | Supply of Rack Mountable VMS +VA Failover Server including licensed Operating system and Anti- virus, complete with all accessories as per specifications. | 1 | Nos. |  |  | 0 | 0 | 0 | 0
400 | Supply of 08 port KVM Switch with integrated 17" LCD/ LED Monitor, for connectivity with Servers in rack as per specifications. | 1 | Nos. |  |  | 0 | 0 | 0 | 0
401 | Supply of Surveillance CCTV 19" Equipment Rack (42 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 1 | Nos. |  |  | 0 | 0 | 0 | 0
402 | Supply of Surveillance CCTV 19" Equipment Rack (9 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 6 | Nos. |  |  | 0 | 0 | 0 | 0
403 | Supply of lifetime licensed VMS and Video Analytics Softwarefor complete system consisting of all Main Servers/all Client Workstations/ NAS, to be supplied with media (2 Nos. of Software CD) to meet the technical & functional requirements as per specifications. | 2 | Set |  |  | 0 | 0 | 0 | 0
404 | Supply of lifetime licensed VMS and Video Analytics Softwarefor complete system consisting of Failover Servers/all Client Workstations/ NAS, to be supplied with media (2 Nos. of Software CD) to meet the technical & functional requirements as per specifications. | 1 | Set |  |  | 0 | 0 | 0 | 0
405 | VMS Camera lifeitime Licence integrated in each Main Server VMS+VA Software. | 120 | Nos |  |  | 0 | 0 | 0 | 0
406 | VMS Camera lifeitime Licence integrated in Failover Server VMS+VA Software. | 120 | Nos |  |  | 0 | 0 | 0 | 0
407 | Video Analytics Camera lifetime License integrated in each Main ServerVMS+VA Software. | 40 | Nos. |  |  | 0 | 0 | 0 | 0
408 | Video Analytics Camera lifetime License integrated in Failover Server VMS+VA Software. | 40 | Nos. |  |  | 0 | 0 | 0 | 0
409 | Supply and laying of Optic Fibre Communication Outdoor cable (6 core, SMF, 9/125 µm, 10 Gbps)in existing pipe on surface/recess/concealed, with connectors/adaptors, termination etc. required as per specifications. | 2000 | Meters |  |  | 0 | 0 | 0 | 0
410 | Supply and laying of CAT-6 UTP Data Cable in existing conduit/pipe on surface/recess/concealed, with connectors, termination etc. required as per specifications. | 5000 | Meters |  |  | 0 | 0 | 0 | 0
411 | Supply and laying of 3 core 6 sqmm multi- strand copper conductor PVC insulated PVC sheathed armouredpower cable on surface/recess/ concealed including termination (at both ends), MCB, distribution box, all accessories etc. required as per specifications. | 3000 | Meters |  |  | 0 | 0 | 0 | 0
412 | Supply of 12 port Light guide Interconnect Unit (LIU)fully populated with modules/ adapters as per siterequirement and specifications. | 7 | Nos. |  |  | 0 | 0 | 0 | 0
413 | Supply and laying of MS Conduit with bends and tees complete with all accessories as per specifications. | 1000 | Meters |  |  | 0 | 0 | 0 | 0
414 | Supply and laying of PVC Conduit with bends and tees complete with all accessories as per specifications. | 2500 | Meters |  |  | 0 | 0 | 0 | 0
415 | Supply of CAT 6 PATCH PANEL complete with all accessories as per specifications. | 6 | Nos. |  |  | 0 | 0 | 0 | 0
416 | Supply of 10 KVA Online UPS with Battery Bank, Power Distribution Panels and complete required accessories as per specifications. | 2 | Nos. |  |  | 0 | 0 | 0 | 0
417 | Supply of Network Time Protocol (NTP) Server with accessories as per specifications. | 1 | No |  |  | 0 | 0 | 0 | 0
418 | Installation,Integration,Testing, Commissioning of the complete SCCTV Systemwith required accessories of all SCCTV equipment properly labelled including networking, cabling etc., configuration of individual equipment as per specifications, training & documentation along with hard copy with drawing/map layout of the entire system including softcopy in Autocad. | 1 | Job |  |  | 0 | 0 | 0 | 0
419 | Supply,Installation of the ANPR Cameras, its Integration with the existing INFINOVA MAKE ANPR Software. | 4 | Nos. |  |  | 0 | 0 | 0 | 0
420 | HHMD and LED TV |  |  |  |  | 0 | 0 | 0 | 0
421 | Supply of 20 HHMD with 5 years warranty. Techno Logy / Dimensiobn Pulse Technology, 350 mm ( Minimum) Length Total (overall) (mm), Less than 350 gm Weight DETECION RANGE / SCAN RATE Ferrous Non Ferrous & Alloy Detection, 25 mm Detects Pin from a minimum distance of (mm) 150 mm Detects Pistol - 0.22 from a minimum distance of (mm): 50 mm Detects Cartridge - 0.22 from a minimum distance of (mm):, 25 mm Detects Razor Blade from a minimum distance of (mm):, Automatic Tuning to ensure equal results on wide range of metals and alloys, 400 mm/s Scan Rate (mm per Second) (mm/s) | 20 | Nos |  |  | 0 | 0 | 0 | 0
422 | Supply of LED Display with mounting arrangement LED Backlit Technology, 138 cm screen size ( Diagonal) Miimum (cm), Non Touch Screen type, In plane switching (IPS) Panel Technology, Portrait and landscape Orientation, 190 x 1080 ( Full HD) Native Resolution ( Pixels), 16:9 Aspect ratio, 450 nits Brightness ( Nits) minimum, 1100:1 bid MAF must Native Contrast Ratio minimum, 178:178 Viewing Angle (Horizontal: vertical), 12 ms Response Time (milli seconds), 11.9 mm Bezel width (mm), 2 Number of Speakers, Inbuilt Arrangement of Speakers, 20 Wattage of Speakers (with maximum 10% THD)(wATT), Avaiable of Output port for audio output if internal speakers are not there, avaiable VGA port HDMI port DVI _ D Port, Display Port, USB Port, RS 232 C port, RJ 45, In built sinage software, 100 w Power Consumption in Operating Mode (Maximum)(Watt), 0.5 Power Consumption in Sleep Mode (Maximum)(Watt), 24 x 7 Duty cycle, Wall mount Mounting aggangement, BIS registration under CRS of meity yes, IF yes BIS registration number R-75000191, ROHS complaiance yes, Power supply 230 V AC 50 Hz, 0 c- 40 C Operation temperature range ( Degree C), Operating Humdity( % RH) 10 %- 80 %, Dimension ( L x Bx H) 1238 x 714 x 54 cm, 50.1 Kg weight, Accessories to be supplied: AC Power cord remote control, user manual, wall mount bracket, necessary cables and connectors yes with on site OEM warrent 05 years | 10 | Nos |  |  | 0 | 0 | 0 | 0
423 | IT works |  |  |  |  | 0 | 0 | 0 | 0
424 | Supply of Layer-2 Switch (Minimum 8 Nos. of 10/100/1000 Mbps PoE+ Copper (Ethernet) Ports (30W per port) and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 2 | Nos. |  |  | 0 | 0 | 0 | 0
425 | Supply of Layer-2 Switch (24 Nos. of 10/100/1000 Mbps Non PoE Copper (Ethernet) Ports and 4 Nos. of 10 Gbps SFP+ ports fully populated with required modules) with 24 Port Jack Panel, SC-LC SM duplex Optic Fiber patch cords and Cat-6 patch cords, Connectors, etc. as required complete as per specifications | 2 | Nos. |  |  | 0 | 0 | 0 | 0
426 | Supply of WiFi Access Points (HP Aruba AP 515) | 8 | Nos. |  |  | 0 | 0 | 0 | 0
427 | Supply of Field Termination Plug Shielded FTP at AP End | 10 | Nos. |  |  | 0 | 0 | 0 | 0
428 | Supply of RJ-45 IO Faceplate with Gang box/Back box with standard length of patch cable, as per site requirement with technical specifications as per bid document. | 40 | Nos. |  |  | 0 | 0 | 0 | 0
429 | Supply of SFP Transceiver 10G with all accessories as per specifications. | 10 | Nos. |  |  | 0 | 0 | 0 | 0
430 | Supply of IT Network Rack 19" Equipment Rack (9 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 3 | Nos. |  |  | 0 | 0 | 0 | 0
431 | Supply of IT Network rack 19" Equipment Rack (18 U) including, power distribution unit, Patch Panel, Cable Manager, cooling fans, accessories, etc. complete as per specifications. | 1 | Nos. |  |  | 0 | 0 | 0 | 0
432 | Supply, laying and splicing of Optic Fibre Communication Outdoor cable (12 core, SMF, 9/125 µm, 10 Gbps) in existing pipe on surface/recess/concealed, with connectors/adaptors, termination etc. required as per specifications. | 2000 | Mtr. |  |  | 0 | 0 | 0 | 0
433 | Supply and laying of CAT-6A UTP Data Cable in existing conduit/pipe on surface/recess/concealed, with connectors, termination etc. required as per specifications. | 5000 | Mtr. |  |  | 0 | 0 | 0 | 0
434 | Supply of 12 port Light guide Interconnect Unit (LIU) fully populated with modules/ adapters as per siterequirement and specifications. | 5 | Mtr. |  |  | 0 | 0 | 0 | 0
435 | Supply of PVC Conduit with bends and tees complete with all accessories as per specifications. | 500 | Mtr. |  |  | 0 | 0 | 0 | 0
436 | Supply of CAT 6A PATCH PANEL complete with all accessories as per specifications. | 6 | Nos. |  |  | 0 | 0 | 0 | 0
437 | Supply of 1 KVA UPS as per specifications. | 4 | Nos. |  |  | 0 | 0 | 0 | 0
438 | Work-Installation,Integration,Testing, Commissioning,Training of the complete system with required accessories of all equipment including networking, cable laying OFC and CAT 6, I/O Boxes etc. configuration of individual equipment as per specifications and integration with the existing system. | 1 | Job |  |  | 0 | 0 | 0 | 0
TOTAL | [6 empty] | 0 | 0 | 0