## Sheet1
Tender Item | Material/Activity Group | Material Name | Technical Specifications | Quantity
Panel Enclosure & Construction | Panel Fabrication | Cubicle Panel | • Type: Form 4B | 1 Set
| [Fabrication, Supplying, Installing] |  | • IP Rating: IP42 (Dust/Vermin proof)
• Sheet: 2 mm CRCA
• Compliance: IS 8623/IEC 60439
• Doors: Hinged, gasketed, lockable
• Accessories: Lifting hooks, Structural reinforcement
| Circuit Breakers (MCCBs) | Incomer MCCBs | • Rating: 400A | 2 Nos.
| [Supplying, Installing] |  | • Poles: 4 Pole
• Breaking Capacity: 36 kA
Trip Type: Thermal Magnetic (O/L, S/C, E/F)
Handle: Rotary extended
|  | Bus-coupler MCCB | • Rating: 400A | 1 No.
• Poles: 4 Pole
• Breaking Capacity: 36 kA
• Trip Type: Thermal Magnetic (O/L, S/C, E/F)
• Interlocking: Mechanical
|  | Outgoing MCCBs | • Ratings: 200A (2 Nos.), 160A (2 Nos.), 100A (4 Nos.), 63A (12 Nos.) | As specified
• Poles: 4 Pole
• Breaking Capacity: 36 kA
• Trip Type: Thermal Magnetic (O/L, S/C, E/F)
• Handle: Rotary
| Busbar System | Aluminum TPN Busbar | • Rating: 400A | 1 Set
| [Supplying, Installing] |  | • Fault withstand: 36 kA (1 sec)
• Insulation: Properly insulated & supported
| Internal Wiring & Interconnections | PVC Copper FRLS Wires | • Sizes: 1.5 & 2.5 sq.mm | As required
| [Supplying, Installing] |  | • Type: PVC insulated Copper FRLS wires
• Application: CTs/control circuits
• Termination: Neatly terminated
|  | Busbar & Cable Connections | • Connections: Properly bolted & secured | Included
• Cable Alley: Adequate size, neatly arranged
| Instrumentation & Accessories | Digital Multifunction Meter | • Type: Digital | 2 Nos.
| [Supplying, Installing] |  | • Accuracy: Class 1.0
|  | Current Transformers (CT) | • Accuracy: Class 1.0 | As required
• Ratio: Suitable as per load
|  | LED Indication Lamps | • Phase Indication: RYB | As required
• Status Indication: ON/OFF/TRIP LED lamps
|  | Control MCB | • Rating: 2A SP | As required
• Breaking Capacity: 10 kA
|  | Labels & Signage | • Type: Numbering | 1 Set
• Labels: Sign-writing, Danger plates
| Mechanical Interlocking | Interlock Mechanism | • Purpose: Prevent simultaneous closure of incomer & bus-coupler | 1 Set
[Supplying, Installing]
| Glands & Earthing Arrangement | Gland Plates | • Thickness: 3 mm | 2 Nos.
| [Supplying, Installing] |  | • Material: CRCA
• Type: Detachable (top & bottom)
|  | Earthing Terminals | • Quantity: 2 Nos. | 2 Nos.
• Rating: Suitable for 36 kA fault level

## Sheet2
Tender Item | Group/Activity Type | Material Name | Technical Specifications | Quantity
Panel Enclosure & Construction | Panel Fabrication [Design, Fabrication, Assembly, Supplying, Erection, Testing, Commissioning] | Cubicle Type Switchboard Panel | • Type: Form 4B | 1 Set
• IP Rating: IP42 (Dust/Vermin proof)
• Sheet: 2 mm CRCA
• Compliance: IS 8623/IEC 60439
• Fault Level: 36 kA (Symmetrical)
• System: 433V, 3-phase, 4-wire, 50Hz
• Doors: Hinged, gasketed, lockable
• Accessories: 3 mm Gland plates (top & bottom), lifting hooks, structural reinforcement
• Earthing: Earth bus, 2 terminals, 36 kA rated
• Finish: 7-tank treated paint (approved shade)
| Circuit Breakers (MCCBs) [Supplying, Installing] | Incomer MCCBs | • Rating: 400A, 4 Pole, 36 kA | 2 Nos.
• Trip Type: Thermal Magnetic (O/L, S/C, E/F)
• Ics Rating: 100% Icu
• Handle: Rotary extended
• Accessories: Spreader link
• Indications: RYB lamp (2 sets), ON/OFF/TRIP lamps (2 sets)
• Control: 2A SP MCB
• Metering: Digital Multifunction Meter & CTs (Class 1.0 accuracy)
|  | Bus-coupler MCCB | • Rating: 400A, 4 Pole, 36 kA | 1 No.
• Trip Type: Thermal Magnetic (O/L, S/C, E/F)
• Ics Rating: 100% Icu
• Handle: Rotary extended
• Accessories: Spreader link
• Indications: ON/OFF/TRIP lamps (1 set)
• Control: 2A SP MCB
• Interlocking: Mechanical with incomers
|  | Outgoing MCCBs | • Ratings: 200A(2), 160A(2), 100A(4), 63A(12) | As specified
• Poles: 4 Pole, 36 kA
• Trip Type: Thermal Magnetic (O/L, S/C, E/F)
• Ics Rating: 100% Icu
• Handle: Rotary extended, spreader links
• Indications: ON/OFF/TRIP lamps (20 sets), RYB LED lamps (all)
• Control: 2A SP MCB
| Busbar System [Supplying, Installing] | TPN Aluminum Alloy Busbar | • Rating: 400A | 1 Set
• Short Circuit: 36kA (1 sec)
• Material: High-conductivity Aluminum Alloy
• Supports: Properly insulated & supported
| Internal Wiring & Interconnections [Supplying, Installing] | Internal Wiring | • Wire: PVC insulated Copper FRLS | As required
• Sizes: 1.8 & 2.6 sq.mm (for CT/control circuits)
• Termination: Neatly dressed & terminated
|  | Busbar & Cable Connections | • Connections: Properly bolted & secured | Included
• Cable Alley: Adequately sized & neatly arranged
| Instrumentation & Accessories [Supplying, Installing] | Digital Multifunction Meter | • Type: Digital | 2 Nos.
• Accuracy: Class 1.0
• Application: Metering for incomers
|  | Current Transformers (CTs) | • Accuracy: Class 1.0 | As required
• Ratio: Suitable for incomer & bus coupler ratings
|  | LED Indication Lamps | • Phase Indication: RYB | As required
• Status Indication: ON/OFF/TRIP LED lamps
|  | Control MCB | • Rating: 2A SP, 10 kA breaking capacity | As required
• Purpose: Lamp & meter control
|  | Labels, Signage & Accessories | • Labels: Numbering, sign-writing, Danger plates | 1 Set
| Mechanical Interlocking [Supplying, Installing] | Mechanical Interlocking Mechanism | • Purpose: Prevent simultaneous closure of incomer & bus-coupler MCCBs | 1 Set
| Glands & Earthing Terminals [Supplying, Installing] | Gland Plates | • Material: CRCA | 2 Nos.
• Thickness: 3 mm
• Location: Detachable, top & bottom
|  |  | • Suitability: Suitable for 36 kA fault level | 2 Nos.
Tender Item | Group / Activity Type<br>[Supplying, Installing] | Material Name (Technical + Minimal Specs) | Sub-Items (with Quantity) | Unit | Main Item Qty
Main LT Panel | Incomer MCCB | Incomer MCCB – 400A, FP, 36 kA | - Extended Rotary Handle for 400A (LV432598_IN) – 2 | Nos. | 2
| [Supplying, Installing] | • Release: Thermal Magnetic (O/L, S/C, E/F) | - Spreader Link 400A FP (LV432493) – 4
|  | • Ics: 100% Icu | - Auxiliary + Alarm Contact (29450) – 4
|  | • Make & Item Code: Schneider, LV540309 | - Indicating Lamp R,Y (Teknik) – 4
- Indicating Lamp B (Teknik) – 2
- Indicating Lamp ON,OFF,TRIP (Teknik) – 6
- Control MCB 2A, SP (A9N1P02C) – 4

## Sheet3
Tender Item | Group/Activity Type<br>[Activity Type] | Material Name | Technical Specifications | Quantity
Aluminum Composite Panel (ACP) Cladding | ACP Cladding [Providing, Fabricating, Installing, Testing, Fixing] | Aluminum Composite Panel | • Type: Metallic colour-coated ACP | 3500 - sqm
• Thickness: 4 mm
• Skin Thickness: 0.5mm (+/-0.5mm)
• Core Material: Mineral core sandwiched between aluminum sheets
• Coating: Kynar 500-based PVDF/Lumiflon resin
• Fire Rating: Class B1, EN 13501 (s1, d0)
• Back Coating: Polymer coating (face #2)
• Panel Weight: Min. 7.5 kg/sq.m
• Protective Film: Self-adhesive peel-off film (60-70 microns)
• Colour: Approved shades SXXX series
• Compliance: EN 13501 Class B1
• Durability: Weather resistant up to 6 months exposure without damage
|  | Aluminum Alloy 6005 T5/MS Brackets | • Material: Aluminum alloy 6005 T5 / Mild Steel (MS) | Included
• Finish: Hot-dip galvanized with serrations
|  | Stainless Steel Screws, Nuts, Bolts, Washers, Cleats | • Material: Stainless steel Grade SS316 | Included
• Colour: Black (matching cladding)
• Components: Screws, nuts, bolts, washers, cleats
|  | Weather Silicone Sealant | • Material: Silicone-based, weatherproof | Included
• Colour: Black (matching cladding)
• Type: Weather-grade silicone sealant
|  | Fasteners, Pins, Anchor Bolts | • Material: SS316 pins, anchor bolts (approved make) | Included
• Application: Wind load arresting, secure fixing
|  | Nylon Separators | • Material: Nylon | Included
• Purpose: Prevent bimetallic corrosion
|  | Base Frame | • Material: Aluminum composite panel, playable type | Included